## ROUND TRAVERSE FORM (3)
ROUND DUCT TRAVERSE FORM
PROJECT: |  | WARABEYA |  |  | SYSTEM: | MUA-4 @53HZ
LOCATION - ZONE: |  | 2nd TRUNK |  |  | SERVICE:
ALTITUDE: |  |  |  | DENSITY: | FACTOR:
DUCT |  |  | REQUIRED |  | ACTUAL
S.P.: |  |  | SCFM: |  | SCFM:
SIZE: | 16in |  | FPM: |  | FPM: | 1855
AREA: | 1.40ft^2 |  | CFM: |  | CFM: | 2598
TEMP:
TEST DATE: |  |  | REMARKS:
2025-09-19
READINGS BY:
AC
1823
1897
1788
1860
1875
1916
1806
1922
1799
1931
1842
1887
1776
1943
1904
1811

## SQUARE TRAVERSE FORM
SQUARE DUCT TRAVERSE FORM
PROJECT | WARABEYA | [5 empty] | SYSTEM | MUA-4 53HZ
LOCATION | 2nd TRUNK | [5 empty] | SERVICE
ALTITUDE | 4 |  | DENSITY | 4 |  |  | FACTOR | 4
DUCT |  |  |  |  | REQUIRED |  |  |  | ACTUAL
S.P. |  |  | TEMP | 4 | SCFM | 4 |  |  | SCFM | 4
SIZE | 16in |  |  |  | FPM |  |  |  | FPM | 1856
AREA | 1.40ft^2 |  |  |  | CFM |  |  |  | CFM | 2598
DISTANCE
FROM | POSITION | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
BOTTOM
1
2
3
4
5
6
7
8
9
10
11
12
13
DISTANCE FROM
DUCT EDGE
VELOCITY
SUB - TOTALS
REMARKS: