## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8750 | 8714 | 7000 | 6995 | 1750 | 1719 | 20% | 19.73%
AC-2 | DINING A | 3300 | 3313 | 2800 | 2779 | 500 | 534 | 15.15% | 16.12%
AC-3 | N DINING B, DT | 4000 | 4177 | 3200 | 3326 | 800 | 851 | 20% | 20.37%
AC-4 | S DINING B | 2890 | 2932 | 2290 | 2286 | 600 | 646 | 20.76% | 22.03%
AC-5 | DINING C | 1800 | 1782 | 1400 | 1365 | 400 | 417 | 22.22% | 23.4%
AC-6 | MULTI-PURPOSE | 1100 | 1109 | 900 | 897 | 200 | 212 | 18.18% | 19.12%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1913 | 1872
EF-2 | HOOD 2 | [10 empty] | 701 | 661
EF-3 | RESTROOM | [12 empty] | 500 | 470
EF-4 | HOOD 3 | [10 empty] | 701 | 716
TOTALS |  | 21840 | 22027 | 17590 | 17648 | 4250 | 4379 |  |  | 0 | 0 | 3315 | 3249 | 500 | 470
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4250 | 4379 |  | FRONT |  | 0.0291 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3815 | 3719 |  | SIDE |  | 0.016 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 435 | 660 |  | REAR |  | 0.014 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0197 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390