## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3300 | 3215 | 2400 | 2283 | 900 | 932 | 27.27% | 28.99%
RTU-2 | KITCHEN | 4900 | 4736 | 2800 | 2571 | 2100 | 2165 | 42.86% | 45.71%
KEF-1 | FRYER | [10 empty] | 860 | 876
KEF-2 | GRILL (SOUTH) | [10 empty] | 738 | 742
KEF-3 | GRILL (NORTH) | [10 empty] | 738 | 761
EF-1 | RESTROOMS | [12 empty] | 150 | 156
TOTALS |  | 8200 | 7951 | 5200 | 4854 | 3000 | 3097 |  |  | 0 | 0 | 2336 | 2379 | 150 | 156
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3000 | 3097 |  | FRONT |  | 0.007 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2486 | 2535 |  | SIDE |  | 0.005 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 514 | 562 |  | REAR |  | 0.006 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.006 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2100 | 2165
TOTAL KITCHEN EXHAUST |  | 2336 | 2379
NET AIRFLOW |  | -236 | -214
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0