## Report Sheet
STORE #: | 4538 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | EAST LIVERPOOL, OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-05-01 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | JORDAN BEST | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
CARRIER | 48HCDD11A2M5A6F4J0 | 4422P67451 | RTU-1 | KITCHEN | 500 | 531 | 0 | 0 |  | 1720 | 17209 | 1029 | 1029 | NL | 212.7 | 212.7 | 3 | 9.2 | 7.26 | 7.26 | 2.5813 | 2.5813 | 0%
CARRIER | 48HCDD11A2M5A6F4J0 | 4422P67370 | RTU-2 | DINING | 1000 | 1570 | 1000 | 1093 |  | 1763 | 1763 | 891 | 891 | NL | 211.9 | 211.9 | 3 | 9.2 | 5.78 | 5.78 | 2.0474 | 2.0474 | 0%
CAPTIVE AIRE | A1-D.250-15D | 5514679 | MUA-1 | HOOD 1 | 1950 | 2066 | 1700 | 1631 | No | 2030 | 1537 | 2030 | 1537 | 2 | 212.7 | 212.9 | 3 | 5.38 | 4.9 | 3.8 | 1.7422 | 1.3524 | -22.38%
CAPTIVE AIRE | DU240HFA | 5514679 | EF-1 | HOOD 1 | 3200 | 1377 | 2450 | 2673 | No | 1102 | 1102 | 1102 | 1102 | 3 | 213.2 | 212.9 | 3 | 9.2 | 8.4 | 5.8 | 2.9937 | 2.0642 | -31.05%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3450 | 4167 | 2700 | 2724 |  | FRONT DOOR |  | -0.094 |  |  | INITIAL | 9.3647 | 4167
|  |  | TOTAL EXHAUST |  | 3350 | 1527 | 2600 | 2823 |  | BACK DOOR |  | 0.047 |  |  | FINAL | 8.0453 | 2724
|  |  | NET AIRFLOW |  | 100 | 2640 | 100 | -99 |  | AVERAGE |  | -0.0235 |  |  | ∆ | 1.3194 | 1443
Issue List
Unit # | Description
Select from drop down list
EF-1 | EF-1 was initially spinning the wrong direction, reversed rotation and it fell within design with no adjustments needed.

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not running / MUA is not running. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.