## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
FC-1.1 | DINING | 1177 | 1108 | 777 | 717 | 400 | 391 | 33.98% | 35.29%
FC-1.2 | DINING | 1177 | 1128 | 777 | 725 | 400 | 403 | 33.98% | 35.73%
FC-2.1 | BACK OF HOUSE | 1130 | 1087 | 1030 | 988 | 100 | 99 | 8.85% | 9.108%
FC-2.2 | BACK OF HOUSE | 1130 | 1012 | 1030 | 918 | 100 | 94 | 8.85% | 9.289%
FC-2.3 | BACK OF HOUSE | 1130 | 909 | 1030 | 808 | 100 | 101 | 8.85% | 11.11%
MUA-1 | COOKLINE | [8 empty] | 2508 | 2174
ESP-1 | KITCHEN HOODS | [10 empty] | 2742 | 2704
EF-1 | RESTROOMS | [12 empty] | 300 | 298
TOTALS |  | 5744 | 5244 | 4644 | 4156 | 1100 | 1088 |  |  | 2508 | 2174 | 2742 | 2704 | 300 | 298
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3608 | 3262 |  | FRONT |  | 0.0052 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3042 | 3002 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 566 | 260 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0052 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2808 | 2468
TOTAL KITCHEN EXHAUST |  | 2742 | 2704
NET AIRFLOW |  | 66 | -236
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0