## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HOOD ON OA |  | HOOD OFF OA |  | HOOD ON EXHAUST |  | HOOD OFF EXHAUST
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU 1 | SALES | 800 | 873 | 350 | 378
RTU-2 | SALES | 800 | 853 | 350 | 378
RTU-3 | BOH/KITCHEN | 800 | 880 | 350 | 344
EF-1 | WOMEN'S RR |  |  |  |  | 225 | 225 | 225 | 225
EF-2 | MEN'S RR |  |  |  |  | 525 | 517 | 525 | 517
EF-3 | HOOD |  |  |  |  | 1350 | 1381 | 0 | 0
TOTALS |  | 2400 | 2606 | 1050 | 1100 | 2100 | 2123 | 750 | 742
HOOD ON
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 2400 | 2606 |  |  | FRONT |  | 0.003 |  | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2100 | 2123 |  |  | SIDE |  | 0.003
NET AIRFLOW |  | 300 | 483 |  |  | REAR |  |  |  | TRUE
[6 empty] | AVERAGE |  | 0.003
HOOD OFF
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20)
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 1050 | 1100 |  |  | FRONT |  | 0.002
TOTAL EXHAUST |  | 750 | 742 |  |  | SIDE |  | 0.004
NET AIRFLOW |  | 300 | 358 |  |  | REAR
[6 empty] | AVERAGE |  | 0.003
NOTES:
OA left on the higher side to make BP positive. Rear door air curtain wouldn't shut off.