## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AHU-1 | OLO LINE | 2500 | 2316 | 2175 | 1980 | 325 | 336 | 13% | 14.51%
AHU-2 | KITCHEN | 2500 | 2416 | 2175 | 2087 | 325 | 329 | 13% | 13.62%
AHU-3 | DINING | 950 | 1865 | 700 | 1591 | 250 | 274 | 26.32% | 14.69%
AHU-4 | DINING | 1325 | 1931 | 975 | 1601 | 350 | 330 | 26.42% | 17.09%
AHU-5 | TRASH ROOM | 335 | 331 | 335 | 331 | 0 | 0 | 0% | 0%
EF-1 | KITCHEN/TRASH RM | [12 empty] | 1010 | 1035
EF-2 | RESTROOM | [12 empty] | 140 | 140
TOTALS |  | 7610 | 8859 | 6360 | 7590 | 1250 | 1269 |  |  | 0 | 0 | 0 | 0 | 1150 | 1175
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1250 | 1269 |  | FRONT |  | 0.002 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1150 | 1175 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 94 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.006 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0