## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN EXHAUST | 4000 | 4071 | 3600 | 3653 | 400 | 418 | 10% | 10.27%
RTU-2 | DINING | 2400 | 2253 | 1855 | 1663 | 545 | 590 | 22.71% | 26.19%
RTU-3 | DINING | 2400 | 2462 | 1855 | 1900 | 545 | 562 | 22.71% | 22.83%
EF-1 | KITCHEN EXHAUST | [10 empty] | 1090 | 1011
EF-2 | TOILET EXHAUST | [12 empty] | 300 | 303
TOTALS |  | 8800 | 8786 | 7310 | 7216 | 1490 | 1570 |  |  | 0 | 0 | 1090 | 1011 | 300 | 303
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1490 | 1570 |  | FRONT |  | 0.0077 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1390 | 1314 |  | SIDE |  | 0.0038 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 256 |  | REAR |  | 0.0028 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0047667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390