## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | BACK ROOM | 1200 | 1126 | 960 | 872 | 240 | 254 | 20% | 22.56%
RTU-2 | KITCHEN | 3000 | 2776 | 2400 | 2135 | 600 | 641 | 20% | 23.09%
RTU-3 | DINING AREA | 5000 | 4430 | 4000 | 3495 | 1000 | 935 | 20% | 21.11%
MUA-1 | HD-1 | [8 empty] | 2350 | 2768
KEF-1 | HD-1 | [10 empty] | 3600 | 4284
EF-3 | W RR | [12 empty] | NA | 112
EF-4 | M RR | [12 empty] | NA | 118
TOTALS |  | 9200 | 8332 | 7360 | 6502 | 1840 | 1830 |  |  | 2350 | 2768 | 3600 | 4284 | 0 | 230
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4190 | 4598 |  | FRONT |  | 0.03 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3600 | 4514 |  | SIDE |  | NA |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 590 | 84 |  | REAR |  | 0.01 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.02 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0