## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
WSHP-1 | KITCHEN | 1600 | 1607 | 1580 | 1585 | 20 | 22 | 1.25% | 1.369%
WSHP-2 | KITCHEN | 1600 | 1728 | 1580 | 1708 | 20 | 20 | 1.25% | 1.157%
WSHP-3 | KITCHEN | 1600 | 1693 | 1600 | 1693 | 0 | 0 | 0% | 0%
ACU-1 | OFFICE |  |  |  |  | 10 | 10 | #DIV/0! | #DIV/0!
MUA-1 | COOKLINE | [8 empty] | 1920 | 1776
PST-1 | HOODS | [10 empty] | 2617 | 2661
TOTALS |  | 4800 | 5028 | 4760 | 4986 | 50 | 52 |  |  | 1920 | 1776 | 2617 | 2661 | 0 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1970 | 1828 |  | FRONT |  | na | [8 empty] | #DIV/0! | #DIV/0! | TRUE
TOTAL EXHAUST |  | 2617 | 2661 |  | SIDE |  | na |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | -647 | -833 |  | REAR |  | na | [8 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL |  |  |  | Notes: Pressure not obtained due to the storefront being open to the mall.
TOTAL KITCHEN OA |  | 1960 | 1818
TOTAL KITCHEN EXHAUST |  | 2617 | 2661
NET AIRFLOW |  | -657 | -843
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0