## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3429 | 2550 | 2517 | 850 | 912 | 25% | 26.6%
AHU-2 | DINING | 4000 | 0 | 3400 | 0 | 600 | 0 | 15% | #DIV/0!
AHU-3 | BASEMENT | 1600 | 1128 | 1450 | 1128 | 150 | 0 | 9.375% | 0%
MUA-1 | KITCHEN HOOD | [8 empty] | 1746 | 1871
EF-1 | KITCHEN HOOD | [10 empty] | 2869 | 2886
EF-2 | RESTROOM | [12 empty] | 150 | 143
TOTALS |  | 9000 | 4557 | 7400 | 3645 | 1600 | 912 |  |  | 1746 | 1871 | 2869 | 2886 | 150 | 143
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 3346 | 2783 |  | FRONT |  | -0.0044 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3019 | 3029 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 327 | -246 |  | REAR |  | -0.0068 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0056 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
[1] AHU-2 is not operational. [2] AHU-3 is existing and does not have an OA connection
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD-1 | CAPTIVE-AIRE |  | SOLO 9 16X16 | [9 empty] | 2869 |  | -2869
HD-2 | CAPTIVE-AIRE | [9 empty] | 1650 |  |  |  | 1650