## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU 31-14 | SALES | 2250 | 2111 | 1750 | 1632 | 500 | 479 | 22.22% | 22.69%
RTU 31-15 | SALES | 2250 | 2289 | 1750 | 1798 | 500 | 491 | 22.22% | 21.45%
RTU 31-16 | BOH | 3000 | 2786 | 2650 | 2445 | 350 | 341 | 11.67% | 12.24%
EF-1 | RESTROOMS | [12 empty] | 175 | 181
EF-2 | IT CLOSET | [12 empty] | 1000 NOT EXHAUST | 1051/NOT EXHAUST
TOTALS |  | 7500 | 7186 | 6150 | 5875 | 1350 | 1311 |  |  | 0 | 0 | 0 | 0 | 175 | 181
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1350 | 1311 |  | FRONT |  | NA | [8 empty] | #DIV/0! | #DIV/0! | FALSE
TOTAL EXHAUST |  | 175 | 181 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 1175 | 1130 |  | REAR |  | NA/NO DOORS | [8 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0