## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3452 | 2650 | 2486 | 750 | 966 | 22.06% | 27.98%
RTU-2 | DINING | 3000 | 3105 | 2250 | 2423 | 750 | 682 | 25% | 21.96%
MUA-1 | KITCHEN HOOD | [8 empty] | 1950 | 1964
EF-1 | KITCHEN HOOD | [10 empty] | 3200 | 3240
EF-2 | RESTROOM | [12 empty] | 150 | 56
TOTALS |  | 6400 | 6557 | 4900 | 4909 | 1500 | 1648 |  |  | 1950 | 1964 | 3200 | 3240 | 150 | 56
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3450 | 3612 |  | FRONT |  | 0.004 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3350 | 3296 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 316 |  | REAR |  | 0.006 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.005 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Due to RTU-2 only being 7.5T, insead of 10T, the design OA were adjusted to 750 each. Otheriwse RTU-2 would be mixing approximately 33% outside air. This adjustment reduces it to 25%.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 183X12 |  | 1950 |  | 3200 |  | -1250