## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | SIDE DINING | 3150 | 3152 | 2400 | 2401 | 750 | 751 | 23.81% | 23.83%
AC-2 | KITCHEN | 8500 | 8577 | 6600 | 6646 | 1900 | 1931 | 22.35% | 22.51%
AC-3 | MAIN DINING | 4000 | 3867 | 3000 | 2833 | 1000 | 1034 | 25% | 26.74%
AC-4 | MAIN DINING | 2750 | 2825 | 2150 | 2196 | 600 | 629 | 21.82% | 22.27%
AC-5 | PLAY AREA | 2000 | 1914 | 1700 | 1627 | 300 | 287 | 15% | 14.99%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 2016
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1416
EF-3 | RESTROOM | [12 empty] | 500 | 496
TOTALS |  | 20400 | 20335 | 15850 | 15703 | 4550 | 4632 |  |  | 0 | 0 | 3314 | 3432 | 500 | 496
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4550 | 4632 |  | FRONT |  | 0.0187 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3814 | 3928 |  | SIDE |  | 0.0185 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 736 | 704 |  | REAR |  | 0.0173 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.018167 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390