## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 7858 | 7500 | 5959 | 2000 | 1899 | 21.05% | 24.17%
AC-2 | SIDE DINNING | 2800 | 2968 | 2240 | 2354 | 560 | 614 | 20% | 20.69%
AC-3 | MAIN DINNING | 4000 | 3977 | 3100 | 3374 | 900 | 603 | 22.5% | 15.16%
AC-4 | DRIVE THRU | 2765 | 2671 | 2205 | 1826 | 560 | 845 | 20.25% | 31.64%
AC-5 | PLAY AREA | 1800 | 1694 | 1440 | 1307 | 360 | 387 | 20% | 22.85%
AC-6 | BOH | 1200 | 1239 | 960 | 1014 | 240 | 225 | 20% | 18.16%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1913 | 1894
EF-2 | HD3 FRYERS | [10 empty] | 701 | 716
EF-3 | RESTROOM | [12 empty] | 400 | 405
EF-4 | HD2 | [10 empty] | 701 | 757
TOTALS |  | 22065 | 20407 | 17445 | 15834 | 4620 | 4573 |  |  | 0 | 0 | 3315 | 3367 | 400 | 405
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4620 | 4573 |  | FRONT |  | 0.027 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3715 | 3772 |  | SIDE |  | 0.024 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 905 | 801 |  | REAR |  | 0.03 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.027 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390