## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3100 | 3099 | 2100 | 2027 | 1000 | 1072 | 32.26% | 34.59%
RTU-2 | KITCHEN | 4800 | 4731 | 2300 | 2195 | 2500 | 2536 | 52.08% | 53.6%
FCU-1 | MANAGER OFFICE |  |  |  |  | 40 | 42 | #DIV/0! | #DIV/0!
KEF-1 | HOOD 1 | [10 empty] | 700 | 716
KEF-2 | HOOD 2 | [10 empty] | 700 | 728
KEF-3 | HOOD 3 | [10 empty] | 700 | 728
KEF-4 | HOOD 4 | [10 empty] | 700 | 740
EF-1 | RESTROOMS | [12 empty] | 300 | 313
TOTALS |  | 7900 | 7830 | 4400 | 4222 | 3540 | 3650 |  |  | 0 | 0 | 2800 | 2912 | 300 | 313
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3540 | 3650 |  | FRONT |  | 0.009 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3100 | 3225 |  | SIDE |  | 0.0011 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 440 | 425 |  | REAR |  | 0.009 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.009 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2540 | 2578
TOTAL KITCHEN EXHAUST |  | 2800 | 2912
NET AIRFLOW |  | -260 | -334
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0