## HP B1-1
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP B1-1 |  | Area: B111
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1700 |  | NEW SA CFM TOTAL
Serial Num | 224611427 |  |  |  | Fan Speed
[5 empty] | RA CFM | 1550
Motor Data |  |  |  |  | RL Voltage | 460
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6
Horsepower | 1 |  |  |  | Suction ESP
Motor Rpm | NL |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 0.6
Voltage (rated) | 460 |  |  |  | Brake HP
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
B11-1 | B112 | S-3 | 10 | 250 |  |  | 0
B11-2 | B112 | S-3 | 10 | 250 |  |  | 0
B11-3 | B112 | S-3 | 10 | 250 |  |  | 0
B11-4 | B110 | S-1 | 6 | 50 |  |  | 0
B11-5 | B108 | S-3 | 10 | 300 |  |  | 0 | CHANGE CFM FROM 200 TO 300
B11-6 | B109 | S-2 | 8 | 150 |  |  | 0
B11-7 | B108 | S-3 | 10 | 225 |  |  | 0
B11-8 | B108 | S-3 | 10 | 225 |  |  | 0
SUPPLY |  |  |  | 1700 |  | 0 | 0
RB11-1 | B110 | R-1 | 6 | 50 |  |  | 0
RB11-2 | B112 | R-5 | 14 | 750 |  |  | 0
RB11-3 | B108 | R-5 | 14 | 600 |  |  | 0
RB11-4 | B109 | R-2 | 8 | 150 |  |  | 0
RETURN |  |  |  | 1550 |  | 0 | 0

## HP B1-2
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP B1-2 |  | Area: B106
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1600
Serial Num | 224611434 |  |  |  | Fan Speed
[5 empty] | RA CFM | 1600
Motor Data |  |  |  |  | RL Voltage | 460
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6
Horsepower | 1 |  |  |  | Suction ESP
Motor Rpm | NL |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 0.6
Voltage (rated) | 460 |  |  |  | Brake HP
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
B12-1 | B107 | S-3 | 10 | 250 |  |  | 0
B12-2 | B107 | S-3 | 10 | 275 |  |  | 0
B12-3 | B107 | S-3 | 10 | 275 |  |  | 0
B12-4 | B105 | S-3 | 10 | 250 |  |  | 0
B12-5 | B105 | S-3 | 10 | 275 |  |  | 0
B12-6 | B105 | S-3 | 10 | 275 |  |  | 0
SUPPLY |  |  |  | 1600 |  | 0 | 0
RB12-1 | B107 | R-5 | 14 | 800 |  |  | 0
RB12-2 | B105 | R-5 | 14 | 800 |  |  | 0
RETURN |  |  |  | 1600 |  | 0 | 0

## HP B1-3
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP B1-3 |  | Area: B103
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1650 | 1691
Serial Num | 224611433 |  |  |  | Fan Speed | - | 1600
[5 empty] | RA CFM | 1600 | 1373
Motor Data |  |  |  |  | RL Voltage | 460 | 484/484/480
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 3.5/3.5//3.6
Horsepower | 1 |  |  |  | Suction ESP | - | -1.23"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.08"
Phase | 3 |  |  |  | Total ESP | 0.6 | 1.31"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.3
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
B113-1 | B104 | S-3 | 10 | 250 | 271 | 255 | 1.02
B113-2 | B104 | S-3 | 10 | 250 | 279 | 253 | 1.012
B113-3 | B104 | S-3 | 10 | 275 | 242 | 278 | 1.0109
B113-4 | B102 | S-1 | 6 | 50 | 163 | 53 | 1.06
B113-5 | B101 | S-3 | 10 | 275 | 233 | 281 | 1.0218
B113-6 | B101 | S-3 | 10 | 275 | 223 | 284 | 1.0327
B113-7 | B101 | S-3 | 10 | 275 | 214 | 285 | 1.0364
SUPPLY |  |  |  | 1650 |  | 1689 | 1.0236
RB13-1 | B104 | R-5 | 14 | 775 | 567 | 660 | 0.85161
RB13-2 | B102 | R-1 | 6 | 50 | 221 | 51 | 1.02
RB13-3 | B101 | R-5 | 14 | 775 | 585 | 662 | 0.85419
RETURN |  |  |  | 1600 |  | 1373 | 0.85813

## HP B1-4
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP B1-4 |  | Area: B114
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1600 | 1639
Serial Num | 224611432 |  |  |  | Fan Speed | - | 1525
[5 empty] | RA CFM | 1600 | 1487
Motor Data |  |  |  |  | RL Voltage | 460 | 483/483/479
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 1.9/1.9/1.8
Horsepower | 1 |  |  |  | Suction ESP | - | -0.41"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.08"
Phase | 3 |  |  |  | Total ESP | 0.6 | 0.49"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.15
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
B14-1 | A134 | S-1 | 6 | 100 | 56 | 100 | 1
B14-2 | B113 | S-3 | 10 | 250 | 155 | 255 | 1.02
B14-3 | B113 | S-3 | 10 | 250 | 130 | 251 | 1.004
B14-4 | B113 | S-3 | 10 | 250 | 121 | 255 | 1.02
B14-5 | B115 | S-3 | 10 | 250 | 200 | 261 | 1.044
B14-6 | B115 | S-3 | 10 | 250 | 176 | 262 | 1.048
B14-7 | B115 | S-3 | 10 | 250 | 80 | 255 | 1.02
SUPPLY |  |  |  | 1600 |  | 1639 | 1.0244
RB14-1 | A134 | R-1 | 6 | 100 | 40 | 91 | 0.91
RB14-2 | B113 | R-5 | 14 | 750 | 703 | 703 | 0.93733
RB14-3 | B115 | R-5 | 14 | 750 | 693 | 693 | 0.924
RETURN |  |  |  | 1600 |  | 1487 | 0.92937

## HP B1-5
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP B1-5 |  | Area: B117
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1600 | 1632
Serial Num | 224411474 |  |  |  | Fan Speed | - | 1500
[5 empty] | RA CFM | 1600 | 1447
Motor Data |  |  |  |  | RL Voltage | 460 | 482/478/481
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 1.9/1.8/1.9
Horsepower | 1 |  |  |  | Suction ESP | - | -0.36"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.09"
Phase | 3 |  |  |  | Total ESP | 0.6 | 0.45"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.15
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
B15-1 | B116 | S-3 | 10 | 250 | 150 | 254 | 1.016
B15-2 | B116 | S-3 | 10 | 275 | 335 | 282 | 1.0255
B15-3 | B116 | S-3 | 10 | 275 | 400 | 280 | 1.0182
B15-4 | B118 | S-3 | 10 | 250 | 140 | 255 | 1.02
B15-5 | B118 | S-3 | 10 | 275 | 80 | 283 | 1.0291
B15-6 | B118 | S-3 | 10 | 275 | 60 | 278 | 1.0109
SUPPLY |  |  |  | 1600 |  | 1632 | 1.02
RB15-1 | B116 | R-5 | 14 | 800 | 756 | 725 | 0.90625
RB15-2 | B118 | R-5 | 14 | 800 | 691 | 722 | 0.9025
RETURN |  |  |  | 1600 |  | 1447 | 0.90438

## HP B1-6
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP B1-6 |  | Area: B123A
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-026 |  |  |  | SA CFM | 800 | 828
Serial Num | 224610906 |  |  |  | Fan Speed | - | 775
[5 empty] | RA CFM | 800 | 828
Motor Data |  |  |  |  | RL Voltage | 265 | 277
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 3.2 | 1.1
Horsepower | 1 |  |  |  | Suction ESP | - | -0.37"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.09"
Phase | 1 |  |  |  | Total ESP | 0.6 | 0.46"
Voltage (rated) | 265 |  |  |  | Brake HP | - | 0.09
Amperage (rated) | 3.2
[5 empty] | VHP-024 | 6 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
B16-1 | B124 | S-4 | 12 | 400 | 123 | 408 | 1.02
B16-2 | B121 | S-2 | 8 | 200 | 140 | 209 | 1.045
B16-3 | B121 | S-2 | 8 | 200 | 250 | 211 | 1.055
SUPPLY |  |  |  | 800 |  | 828 | 1.035
RB16-1 | B124 | R-4 | 12 | 400 | 408 | 408 | 1.02
RB16-2 | B121 | R-2 | 8 | 400 | 420 | 420 | 1.05
RETURN |  |  |  | 800 |  | 828 | 1.035

## HP B1-7
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP B1-7 |  | Area: B123A
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-012 |  |  |  | SA CFM | 400 | 420
Serial Num | 224310537 |  |  |  | Fan Speed | - | LOW
[5 empty] | RA CFM | 400 | 420
Motor Data |  |  |  |  | RL Voltage | 265 | 280
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 0.7 | 0.4
Horsepower | 1 |  |  |  | Suction ESP | - | -0.08"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.05"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.13"
Voltage (rated) | 265 |  |  |  | Brake HP | - | 0.08
Amperage (rated) | 0.7
[5 empty] | VHP-012 | 2.5 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
B17-1 | B128 | S-1 | 6 | 50 | 75 | 55 | 1.1
B17-2 | B129 | S-1 | 6 | 50 | 78 | 55 | 1.1
B17-3 | A134 | S-2 | 8 | 150 | 198 | 157 | 1.0467
B17-4 | B119 | S-2 | 8 | 150 | 201 | 153 | 1.02
SUPPLY |  |  |  | 400 |  | 420 | 1.05
RB17-1 | B119 | R-2 | 8 | 150 | 120 | 120 | 0.8
RB17-2 | A134 | R-3 | 10 | 250 | 205 | 205 | 0.82
RETURN |  |  |  | 400 |  | 325 | 0.8125

## HP A1-1
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP A1-1 |  | Area: A124
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-006 |  |  |  | SA CFM | 200
Serial Num | 224411021 |  |  |  | Fan Speed
[5 empty] | OA CFM | 30
[5 empty] | RA CFM | 170 |  | NEW RA TOTAL CFM
Motor Data |  |  |  |  | RL Voltage | 265
Motor MFG | US Motors |  |  |  | RL Amperage | 0.4
Horsepower | 0.04 |  |  |  | Suction ESP
Motor Rpm | 1500 |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP | 0.7
Voltage (rated) | 265 |  |  |  | Brake HP
Amperage (rated) | 0.4
[5 empty] | VHP-006 | 1.25 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
A11-1 | A119 | S-1 | 6 | 25 |  |  | 0
A11-2 | A115 | S-1 | 6 | 75 |  |  | 0
A11-3 | A121 | S-1 | 6 | 25 |  |  | 0
A11-4 | A122 | S-1 | 6 | 75 |  |  | 0
SUPPLY |  |  |  | 200 |  | 0 | 0
OA FROM DOAS | A1-1 | DUCT |  | 30 |  |  | 0
OA |  |  |  | 30 |  | 0 | 0
RA11-1 | A115 | R-1 | 6 | 95 |  |  | 0 | CHANGE CFM FROM 100 TO 95
RA11-2 | A122 | R-1 | 6 | 75 |  |  | 0
RETURN |  |  |  | 170 |  | 0 | 0
NOTES: | 30 CFM OA FROM DOAS DUCTED TO RA VIA DAMPER
HP DESIGN IS 168 CFM, SGRD TOTAL IS 200 CFM, RETURN+OA TOTAL IS 200 CFM

## HP A1-2
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP A1-2 |  | Area: B100
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-009 |  |  |  | SA CFM | 300 | 348
Serial Num | 224310531 |  |  |  | Fan Speed | - | LOW
[5 empty] | RA CFM | 300 | 348
Motor Data |  |  |  |  | RL Voltage | 265 | 278
Motor MFG | US Motors |  |  |  | RL Amperage | 0.4 | 0.2
Horsepower | 0.05 |  |  |  | Suction ESP
Motor Rpm | 1680 |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP | 0.7
Voltage (rated) | 265 |  |  |  | Brake HP
Amperage (rated) | 0.4
[5 empty] | VHP-009 | 1.88 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
A112-1 | A118 | S-3 | 10 | 300 | 379 | 348 | 1.16
SUPPLY |  |  |  | 300 |  | 348 | 1.16
RA12-1 | A118 | R-3 | 10 | 300 | 379 | 348 | 1.16
RETURN |  |  |  | 300 |  | 348 | 1.16
NOTES: | HP DESIGNED FOR 230 CFM, SGRD TOTAL IS 300, EGRD TOTAL IS 300

## HP A1-3
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP A1-3 |  | Area: A124
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-012 |  |  |  | SA CFM | 400
Serial Num | 224310536 |  |  |  | Fan Speed
[5 empty] | OA CFM | 70
[5 empty] | RA CFM | 330 |  | NEW RA CFM TOTAL
Motor Data |  |  |  |  | RL Voltage | 265
Motor MFG | US Motors |  |  |  | RL Amperage | 0.7
Horsepower | 0.14 |  |  |  | Suction ESP
Motor Rpm | 1680 |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP | 0.4
Voltage (rated) | 265 |  |  |  | Brake HP
Amperage (rated) | 0.7
[5 empty] | VHP-012 | 2.50 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
A13-1 | A117 | S-2 | 8 | 200 |  |  | 0
A13-2 | A117 | S-2 | 8 | 200 |  |  | 0
SUPPLY |  |  |  | 400 |  | 0 | 0
OA FROM DOAS | A1-3 | DUCT |  | 70 |  |  | 0
OA |  |  |  | 70 |  | 0 | 0
RA13-1 | A117 | R-4 |  | 330 |  |  | 0 | CHANGE FROM 200 TO 330 CFM
RETURN |  |  |  | 330 |  | 0 | 0
NOTES: | 70 CFM OA FROM DOAS DUCTED TO RA VIA DAMPER

## HP A1-4
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP A1-4 |  | Area: A124
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-006 |  |  |  | SA CFM | 200
Serial Num | 224411023 |  |  |  | Fan Speed
[5 empty] | RA CFM | 200
Motor Data |  |  |  |  | RL Voltage | 265
Motor MFG | US Motors |  |  |  | RL Amperage | 0.4
Horsepower | 0.04 |  |  |  | Suction ESP
Motor Rpm | 1500 |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP | 0.7
Voltage (rated) | 265 |  |  |  | Brake HP
Amperage (rated) | 0.4
[5 empty] | VHP-006 | 1.25 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
A14-1 | A125 | S-2 | 8 | 200 |  |  | 0
SUPPLY |  |  |  | 200 |  | 0 | 0
RA14-1 | A125 | R-2 | 8 | 200 |  |  | 0
RETURN |  |  |  | 200 |  | 0 | 0
NOTES: | HP DESIGN IS 168 CFM, SGRD TOTAL IS 200 CFM, EGRD TOTAL IS 200 CFM

## HP A1-5
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP A1-5 |  | Area: A124
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-038 |  |  |  | SA CFM | 1200
Serial Num | 225011006 |  |  |  | Fan Speed
[5 empty] | RA CFM | 1200
Motor Data |  |  |  |  | RL Voltage | 460
Motor MFG | Perfect Speed |  |  |  | RL Amperage | 3.2
Horsepower | 0.5 |  |  |  | Suction ESP
Motor Rpm | NL |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 0.6
Voltage (rated) | 460 |  |  |  | Brake HP
Amperage (rated) | 3.2
[5 empty] | VHP-036 | 9 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
A15-1 | A100 | S-12 | 16X8 | 300 |  |  | 0
A15-2 | A100 | S-12 | 16X8 | 300 |  |  | 0
A15-3 | A100 | S-12 | 16X8 | 300 |  |  | 0
A15-4 | A001 | S-12 | 16X8 | 300 |  |  | 0
SUPPLY |  |  |  | 1200 |  | 0 | 0
RA15-1 | A134 | R-4 | 12 | 1200 |  |  | 0
RETURN |  |  |  | 1200 |  | 0 | 0

## HP A1-6
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP A1-6 |  | Area: A108
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-006 |  |  |  | SA CFM | 200
Serial Num | 224411022 |  |  |  | Fan Speed
[5 empty] | OA CFM | 55
[5 empty] | RA CFM | 145
Motor Data |  |  |  |  | RL Voltage | 265
Motor MFG | US MOTORS |  |  |  | RL Amperage | 0.4
Horsepower | 0.04 |  |  |  | Suction ESP
Motor Rpm | 1500 |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP | 0.7
Voltage (rated) | 265 |  |  |  | Brake HP
Amperage (rated) | 0.4
[5 empty] | VHP-006 | 1.25 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
A16-1 | A102 | S-1 | 6 | 75 |  |  | 0
A16-2 | A102 | S-1 | 6 | 50 |  |  | 0
A16-3 | A103 | S-2 | 8 | 75 |  |  | 0
SUPPLY |  |  |  | 200 |  | 0 | 0
OA FROM DOAS | A1-6 | DUCT |  | 55 |  |  | 0
OA |  |  |  | 55 |  | 0 | 0
RA16-1 | A102 | R-2 | 8 | 200 |  |  | 0
RETURN |  |  |  | 200 |  | 0 | 0
NOTES: | 55 CFM OA FROM DOAS DUCTED TO RA VIA DAMPER
HP DESIGN IS 168 CFM, SGRD TOTAL IS 200 CFM, EGRD TOTAL IS 200 CFM

## HP A1-7
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP A1-7 |  | Area: A108
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-012 |  |  |  | SA CFM | 400
Serial Num | 224310535 |  |  |  | Fan Speed
[5 empty] | OA CFM | 105
[5 empty] | RA CFM | 400
Motor Data |  |  |  |  | RL Voltage | 265
Motor MFG | US MOTORS |  |  |  | RL Amperage | 0.7
Horsepower | 0.14 |  |  |  | Suction ESP
Motor Rpm | 1625 |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP | 0.4
Voltage (rated) | 265 |  |  |  | Brake HP
Amperage (rated) | 0.7
VHP-012
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
A17-1 | A106 | S-1 | 6 | 100 |  |  | 0
A17-2 | A101 | S-2 | 8 | 150 |  |  | 0
A17-3 | A101 | S-2 | 8 | 150 |  |  | 0
SUPPLY |  |  |  | 400 |  | 0 | 0
OA FROM DOAS | A1-7 | DUCT |  | 105 |  |  | 0
OA |  |  |  | 105 |  | 0 | 0
RA17-1 | A106 | R-2 |  | 100 |  |  | 0
RA17-2 | A101 | R-1 |  | 300 |  |  | 0
RETURN |  |  |  | 400 |  | 0 | 0
NOTES: | 105 CFM OA FROM DOAS DUCTED TO RA VIA DAMPER

## HP A1-8
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP A1-8 |  | Area: A108
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-009 |  |  |  | SA CFM | 300
Serial Num | 224310532 |  |  |  | Fan Speed
[5 empty] | OA CFM | 80
[5 empty] | RA CFM | 300
Motor Data |  |  |  |  | RL Voltage | 265
Motor MFG | US MOTORS |  |  |  | RL Amperage | 0.4
Horsepower | 0.05 |  |  |  | Suction ESP
Motor Rpm | 1580 |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP | 0.7
Voltage (rated) | 265 |  |  |  | Brake HP
Amperage (rated) | 0.4
[5 empty] | VHP-009 | 1.88 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
A18-1 | A109 | S-1 | 6 | 50 |  |  | 0
A18-2 | A111 | S-1 | 6 | 75 |  |  | 0
A18-3 | A113 | S-1 | 6 | 75 |  |  | 0
A18-4 | A110 | S-1 | 6 | 100 |  |  | 0
SUPPLY |  |  |  | 300 |  | 0 | 0
OA FROM DOAS | A1-8 | DUCT |  | 80 |  |  | 0
OA |  |  |  | 80 |  | 0 | 0
RA18-1 | A109 | R-1 | 6 | 75 |  |  | 0
RA18-2 | A111 | R-1 | 6 | 75 |  |  | 0
RA18-3 | A110 | R-1 | 6 | 50 |  |  | 0
RA18-4 | A113 | R-1 | 6 | 100 |  |  | 0
RETURN |  |  |  | 300 |  | 0 | 0
NOTES: | 80 CFM OA FROM DOAS DUCTED TO RA VIA DAMPER
HP DESIGNED FOR 230 CFM, SGRD TOTAL IS 300, EGRD TOTAL IS 300

## HP A1-9
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP A1-9 |  | Area: E103
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-26 |  |  |  | SA CFM | 900 | 919 | NEW SA TOTAL CFM
Serial Num | 224610905 |  |  |  | Fan Speed |  | 875
[5 empty] | RA CFM | 800 | 898
Motor Data |  |  |  |  | RL Voltage | 265 | 276
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 3.2 | 1.3
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.21"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.1"
Phase | 1 |  |  |  | Total ESP | 0.6 | 0.31"
Voltage (rated) | 265 |  |  |  | Brake HP |  | 0.05
Amperage (rated) | 3.2
[5 empty] | VHP-024 | 6 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
A19-1 | A126 | S-3 | 10 | 300 | 163 | 308 | 1.0267
A19-2 | A126 | S-3 | 10 | 300 | 251 | 303 | 1.01
A19-3 | A126 | S-3 | 10 | 300 | 132 | 308 | 1.0267 | CHANGE FROM 200 TO 300 CFM
SUPPLY |  |  |  | 900 |  | 919 | 1.0211
RA19-1 | A126 | R-5 | 14 | 800 | 501 | 898 | 1.1225
RETURN |  |  |  | 800 |  | 898 | 1.1225

## HP A1-10
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP A1-10 |  | Area: E103
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-012 |  |  |  | SA CFM | 400 | 379
Serial Num | 224310534 |  |  |  | Fan Speed | - | LOW
[5 empty] | RA CFM | 400 | 379
Motor Data |  |  |  |  | RL Voltage | 265 | 282
Motor MFG | US MOTORS |  |  |  | RL Amperage | 0.7 | 0.4
Horsepower | 0.14 |  |  |  | Suction ESP | - | -0.13
Motor Rpm | 1625 |  |  |  | Discharge ESP | - | 0.03
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.16
Voltage (rated) | 265 |  |  |  | Brake HP | - | 0.01
Amperage (rated) | 0.7
[5 empty] | VHP-012 | 2.5 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
A110-1 | A131 | S-1 | 6 | 50 | 48 | 46 | 0.92
A110-2 | A129 | S-2 | 8 | 175 | 174 | 167 | 0.95429
A110-3 | A29 | S-2 | 8 | 175 | 173 | 166 | 0.94857
SUPPLY |  |  |  | 400 |  | 379 | 0.9475
RA110-1 | A131 | R-1 | 6 | 50 | 95 | 46 | 0.92
RA110-2 | A129 | R-3 | 10 | 350 | 353 | 286 | 0.81714
RETURN |  |  |  | 400 |  | 332 | 0.83

## HP A1-11
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP A1-11 |  | Area: E103
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-026 |  |  |  | SA CFM | 750 | 791 | NEW SA TOTAL CFM
Serial Num | 224610907 |  |  |  | Fan Speed | -
[5 empty] | RA CFM | 800 | 818
Motor Data |  |  |  |  | RL Voltage | 265 | 282
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 3.2 | 1.1
Horsepower | 0.5 |  |  |  | Suction ESP | - | -0.27"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.18"
Phase | 1 |  |  |  | Total ESP | 0.6 | 0.45"
Voltage (rated) | 265 |  |  |  | Brake HP | - | 0.04
Amperage (rated) | 3.2
[5 empty] | VHP-024 | 6 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
A111-1 | A128 | S-3 | 10 | 250 | 278 | 263 | 1.052 | CHANGE FROM 275 TO 250 CFM
A111-2 | A128 | S-3 | 10 | 250 | 282 | 267 | 1.068 | CHANGE FROM 275 TO 250 CFM
A111-3 | A128 | S-3 | 10 | 250 | 258 | 261 | 1.044
SUPPLY |  |  |  | 750 |  | 791 | 1.0547
RA111-1 | A128 | R-5 | 14 | 800 | 818 | 791 | 0.98875
RETURN |  |  |  | 800 |  | 791 | 0.98875

## HP A1-12
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP A1-12 |  | Area: E103
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1650 | 1697
Serial Num | 224611429 |  |  |  | Fan Speed | - | 1600
[5 empty] | RA CFM | 1600 | 1697
Motor Data |  |  |  |  | RL Voltage | 460 | 490/486/490
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 2.8/2.8/2.7
Horsepower | 1 |  |  |  | Suction ESP | - | -0.77"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.19"
Phase | 3 |  |  |  | Total ESP | 0.6 | 0.96"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.23
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
A112-1 | A130 | S-2 | 8 | 175 | 134 | 181 | 1.0343
A112-2 | A130 | S-2 | 8 | 175 | 77 | 179 | 1.0229
A112-3 | A130 | S-2 | 8 | 175 | 88 | 182 | 1.04
A112-4 | A130 | S-5 | 14 | 200 | 90 | 202 | 1.01
A112-5 | A130 | S-2 | 8 | 175 | 136 | 181 | 1.0343
A112-6 | A130 | S-2 | 8 | 175 | 119 | 180 | 1.0286
A112-7 | A130 | S-2 | 8 | 175 | 119 | 182 | 1.04
A112-8 | A130 | S-5 | 14 | 200 | 27 | 206 | 1.03
A112-9 | A130 | S-5 | 14 | 200 | 116 | 204 | 1.02
SUPPLY |  |  |  | 1650 |  | 1697 | 1.0285
RA112-1 | A130 | R-9 | 46X22 | 1600 | 912 | 1697 | 1.0606
RETURN |  |  |  | 1600 |  | 1697 | 1.0606

## HP A1-13
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP A1-13 |  | Area: C130
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-26 |  |  |  | SA CFM | 850 | 869 | NEW SA TOTAL CFM
Serial Num | 224610908 |  |  |  | Fan Speed | - | 825
[5 empty] | RA CFM | 700 | 869
Motor Data |  |  |  |  | RL Voltage | 265 | 276
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 3.2 | 1
Horsepower | 0.5 |  |  |  | Suction ESP | - | -0.20"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.02"
Phase | 1 |  |  |  | Total ESP | 0.6 | 0.22"
Voltage (rated) | 265 |  |  |  | Brake HP | - | 0.04
Amperage (rated) | 3.2
[5 empty] | VHP-024 | 6 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
A113-1 | A132 | S-3 | 10 | 250 | 65 | 257 | 1.028
A113-2 | A132 | S-1 | 6 | 100 | 0 | 103 | 1.03
A113-3 | A132 | S-3 | 10 | 250 | 398 | 255 | 1.02 | CHANGE FROM 275 TO 250 CFM
A113-4 | A132 | S-3 | 10 | 250 | 393 | 254 | 1.016
SUPPLY |  |  |  | 850 |  | 869 | 1.0224
RA113-1 | A132 | R-5 | 14 | 700 | 856 | 869 | 1.2414
RETURN |  |  |  | 700 |  | 869 | 1.2414

## HP C1-1
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP C1-1 |  | Area: C103
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-012 |  |  |  | SA CFM | 400 | 382
Serial Num | 224310540 |  |  |  | Fan Speed | - | LOW
[5 empty] | RA CFM | 400 | 382
Motor Data |  |  |  |  | RL Voltage | 265 | 275
Motor MFG | US MOTORS |  |  |  | RL Amperage | 0.7 | 0.4
Horsepower | 0.14 |  |  |  | Suction ESP | - | -0.09"
Motor Rpm | 1625 |  |  |  | Discharge ESP | - | 0.02"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.11"
Voltage (rated) | 265 |  |  |  | Brake HP | - | 0.08
Amperage (rated) | 0.7
[5 empty] | VHP-012 | 2.5 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C11-1 | C104 | S-2 | 8 | 200 | 350 | 196 | 0.98
C11-2 | C104 | S-2 | 8 | 200 | 0 | 186 | 0.93
SUPPLY |  |  |  | 400 |  | 382 | 0.955
RC11-1 | C104 | R-4 | 12 | 400 | 350 | 382 | 0.955
RETURN |  |  |  | 400 |  | 382 | 0.955

## HP C1-2
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP C1-2 |  | Area: C103
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-026 |  |  |  | SA CFM | 800
Serial Num | 224610913 |  |  |  | Fan Speed
[5 empty] | RA CFM | 800 |  | NEW RA CFM TOTAL
Motor Data |  |  |  |  | RL Voltage | 265
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 3.2
Horsepower | 0.5 |  |  |  | Suction ESP
Motor Rpm | NL |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP | 0.6
Voltage (rated) | 265 |  |  |  | Brake HP
Amperage (rated) | 3.2
[5 empty] | VHP-024 | 6 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C12-1 | C102 | S-1 | 6 | 100 |  |  | 0
C12-2 | C105 | S-3 | 10 | 250 |  |  | 0
C12-3 | C105 | S-3 | 10 | 200 |  |  | 0
C12-4 | C105 | S-3 | 10 | 250 |  |  | 0
SUPPLY |  |  |  | 800 |  | 0 | 0
RC12-1 | C102 | R-1 | 6 | 100 |  |  | 0
RC12-2 | C105 | R-5 | 14 | 700 |  |  | 0 | CHANGE CFM FROM 800 TO 700
RETURN |  |  |  | 800 |  | 0 | 0

## HP C1-3
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP C1-3 |  | Area: C107
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1600 | 1650
Serial Num | 224611438 |  |  |  | Fan Speed | - | 1500
[5 empty] | RA CFM | 1400 | 1473 | NEW RA CFM TOTAL
Motor Data |  |  |  |  | RL Voltage | 460 | 470/468/472
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 1.9/1.8/1.9
Horsepower | 1 |  |  |  | Suction ESP | - | -0.33"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.07"
Phase | 3 |  |  |  | Total ESP | 0.6 | 0.40"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.15
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C13-1 | C106 | S-3 | 10 | 250 | 287 | 260 | 1.04
C13-2 | C106 | S-3 | 10 | 275 | 267 | 278 | 1.0109
C13-3 | C106 | S-3 | 10 | 275 | 245 | 282 | 1.0255
C13-4 | C108 | S-3 | 10 | 250 | 287 | 264 | 1.056
C13-5 | C108 | S-3 | 10 | 275 | 287 | 285 | 1.0364
C13-6 | C108 | S-3 | 10 | 275 | 265 | 281 | 1.0218
SUPPLY |  |  |  | 1600 |  | 1650 | 1.0312
RC13-1 | C106 | R-5 | 14 | 700 | 750 | 742 | 1.06 | CHANGE CFM FROM 800 TO 700
RC13-2 | C108 | R-5 | 14 | 700 | 730 | 731 | 1.0443 | CHANGE CFM FROM 800 TO 700
RETURN |  |  |  | 1400 |  | 1473 | 1.0521

## HP C1-4
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP C1-4 |  | Area: C110
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1600
Serial Num |  |  |  |  | Fan Speed
[5 empty] | RA CFM | 1400 |  | NEW RA CFM TOTAL
Motor Data |  |  |  |  | RL Voltage | 460
Motor MFG |  |  |  |  | RL Amperage | 6
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 0.6
Voltage (rated) | 460 |  |  |  | Brake HP
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C14-1 | C109 | S-3 | 10 | 250 |  |  | 0
C14-2 | C109 | S-3 | 10 | 275 |  |  | 0
C14-3 | C109 | S-3 | 10 | 275 |  |  | 0
C14-4 | C111 | S-3 | 10 | 250 |  |  | 0
C14-5 | C111 | S-3 | 10 | 275 |  |  | 0
C14-6 | C111 | S-3 | 10 | 275 |  |  | 0
SUPPLY |  |  |  | 1600 |  | 0 | 0
RC14-1 | C109 | R-5 | 14 | 700 |  |  | 0 | CHANGE CFM FROM 800 TO 700
RC14-2 | C111 | R-5 | 14 | 700 |  |  | 0 | CHANGE CFM FROM 800 TO 700
RETURN |  |  |  | 1400 |  | 0 | 0

## HP C1-5
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP C1-5 |  | Area: C130
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-009 |  |  |  | SA CFM | 300 | 370
Serial Num | 224411026 |  |  |  | Fan Speed | - | LOW
[5 empty] | RA CFM | 300 | 287
Motor Data |  |  |  |  | RL Voltage | 265 | 273
Motor MFG | US MOTORS |  |  |  | RL Amperage | 0.4 | 0.2
Horsepower | 0.05 |  |  |  | Suction ESP | - | -0.14"
Motor Rpm | 1580 |  |  |  | Discharge ESP | - | 0.22"
Phase | 1 |  |  |  | Total ESP | 0.7 | 0.36
Voltage (rated) | 265 |  |  |  | Brake HP | - | 0.002
Amperage (rated) | 0.4
[5 empty] | VHP-009 | 1.88 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C15-1 | C128 | S-1 | 6 | 50 | 95 | 61 | 1.22
C15-2 | C127 | S-1 | 6 | 50 | 95 | 61 | 1.22
C15-3 | A134 | S-1 | 6 | 100 | 103 | 123 | 1.23
C15-4 | C119 | S-1 | 6 | 100 | 115 | 124 | 1.24
SUPPLY |  |  |  | 300 |  | 369 | 1.23
RC15-1 | A134 | R-2 | 8 | 200 | 263 | 204 | 1.02
RC15-2 | A134 | R-1 | 6 | 100 | 145 | 83 | 0.83
RETURN |  |  |  | 300 |  | 287 | 0.95667
NOTES: | HP DESIGNED FOR 230 CFM, SGRD TOTAL IS 300, EGRD TOTAL IS 300

## HP C1-6
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP C1-6 |  | Area: C130
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-012 |  |  |  | SA CFM | 400 | 385
Serial Num | 224310533 |  |  |  | Fan Speed | - | LOW
[5 empty] | RA CFM | 400 | 385
Motor Data |  |  |  |  | RL Voltage | 265 | 274
Motor MFG | US MOTORS |  |  |  | RL Amperage | 0.7 | 0.4
Horsepower | 0.14 |  |  |  | Suction ESP | - | -0.11"
Motor Rpm | 1625 |  |  |  | Discharge ESP | - | 0.03"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.14"
Voltage (rated) | 265 |  |  |  | Brake HP | - | 0.08
Amperage (rated) | 0.7
[5 empty] | VHP-012 | 2.5 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C16-1 | C123 | S-4 | 12 | 400 | 457 | 385 | 0.9625
SUPPLY |  |  |  | 400 |  | 385 | 0.9625
RC16-1 | C123 | R-3 | 10 | 400 | 457 | 385 | 0.9625
RETURN |  |  |  | 400 |  | 385 | 0.9625

## HP C1-7
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP C1-7 |  | Area: C118
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1600 | 1662
Serial Num | 224611439 |  |  |  | Fan Speed | - | 1550
[5 empty] | RA CFM | 1600 | 1442
Motor Data |  |  |  |  | RL Voltage | 460 | 478/475/473
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 2.1/2.0/2.1
Horsepower | 1 |  |  |  | Suction ESP | 0.6 | -0.35"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.08"
Phase | 3 |  |  |  | Total ESP | - | 0.43"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.2
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C17-1 | C117 | S-2 | 8 | 200 | 266 | 209 | 1.045
C17-2 | C117 | S-3 | 10 | 250 | 256 | 259 | 1.036
C17-3 | C117 | S-3 | 10 | 250 | 280 | 261 | 1.044
C17-4 | C121 | S-2 | 8 | 150 | 196 | 155 | 1.0333
C17-5 | C120 | S-1 | 6 | 50 | 107 | 53 | 1.06
C17-6 | C122 | S-2 | 8 | 200 | 175 | 206 | 1.03
C17-7 | C122 | S-3 | 10 | 250 | 305 | 261 | 1.044
C17-8 | C122 | S-3 | 10 | 250 | 84 | 258 | 1.032
SUPPLY |  |  |  | 1600 |  | 1662 | 1.0388
RC17-1 | C117 | R-5 | 14 | 700 | 1000 | 622 | 0.88857
RC17-2 | C120 | R-1 | 6 | 50 | 68 | 49 | 0.98
RC17-3 | C121 | R-2 | 8 | 150 | 130 | 143 | 0.95333
RC17-4 | C122 | R-5 | 14 | 700 | 223 | 628 | 0.89714
RETURN |  |  |  | 1600 |  | 1442 | 0.90125

## HP C1-8
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP C1-8 |  | Area: C115
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1600 | 1639
Serial Num | 23011059 |  |  |  | Fan Speed | - | 1725
[5 empty] | RA CFM | 1400 |  | NEW RA CFM TOTAL
Motor Data |  |  |  |  | RL Voltage | 460 | 480/470/481
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 3.0/2.1/2.6
Horsepower | 1 |  |  |  | Suction ESP | - | -0.77"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.02"
Phase | 3 |  |  |  | Total ESP | 0.6 | 0.79"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.24
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C18-1 | C114 | S-3 | 10 | 250 | 0 | 259 | 1.036
C18-2 | C114 | S-3 | 10 | 275 | 300 | 278 | 1.0109
C18-3 | C114 | S-3 | 10 | 275 | 0 | 280 | 1.0182
C18-4 | C116 | S-3 | 10 | 250 | 400 | 262 | 1.048
C18-5 | C116 | S-3 | 10 | 275 | 216 | 282 | 1.0255
C18-6 | C116 | S-3 | 10 | 275 | 287 | 278 | 1.0109
SUPPLY |  |  |  | 1600 |  | 1639 | 1.0244
RC18-1 | C116 | R-5 | 14 | 700 |  |  | 0 | CHANGE CFM FROM 800 TO 700
RC18-2 | C114 | R-5 | 14 | 700 |  |  | 0 | CHANGE CFM FROM 800 TO 700
RETURN |  |  |  | 1400 |  | 0 | 0

## HP D1-1
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP D1-1 |  | Area: D111
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1600 | 1644
Serial Num | 231311343 |  |  |  | Fan Speed | - | 1700
[5 empty] | RA CFM | 1600 | 1647
Motor Data |  |  |  |  | RL Voltage | 460 | 478/480/481
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 3.8/3.8/3.7
Horsepower | 1 |  |  |  | Suction ESP | - | -0.88"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.15"
Phase | 3 |  |  |  | Total ESP | 0.6 | 1.03"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.31
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
D11-1 | D109 | S-10 | 18X6 | 400 | 376 | 411 | 1.0275
D11-2 | D109 | S-10 | 18X6 | 400 | 376 | 411 | 1.0275
D11-3 | D109 | S-10 | 18X6 | 400 | 376 | 411 | 1.0275
D11-4 | D109 | S-10 | 18X6 | 400 | 376 | 411 | 1.0275
SUPPLY |  |  |  | 1600 | (TRAVERSE) | 1644 | 1.0275
RD11-1 | D110 | R-13 | 72X12 | 1600 | 1504 | 1644 | 1.0275
RETURN |  |  |  | 1600 |  | 1644 | 1.0275

## HP D1-2
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP D1-2 |  | Area: D111
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1650 | 1648
Serial Num | 224611426 |  |  |  | Fan Speed | - | 1950
[5 empty] | RA CFM | 100 | 1648 | NEW RA CFM TOTAL
Motor Data |  |  |  |  | RL Voltage | 460 | 477/476/479
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 5.5/5.4/5.5
Horsepower | 1 |  |  |  | Suction ESP | - | -1.65"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.16"
Phase | 3 |  |  |  | Total ESP | 0.6 | 1.81"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.46
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
D12-1 | D110 | S-2 | 8 | 200 | 179 | 202 | 1.01
D12-2 | D112 | S-1 | 6 | 50 | 220 | 54 | 1.08
D12-3 | D113 | S-1 | 6 | 100 |  | 102 | 1.02
D12-4 | D110 | S-1 | 6 | 100 | 91 | 100 | 1
D12-5 | D118 | S-1 | 6 | 100 | 92 | 98 | 0.98
D12-6 | D119 | S-1 | 6 | 100 | 93 | 97 | 0.97
D12-7 | D120 | S-4 | 12 | 400 | 380 | 395 | 0.9875
D12-8 | D122 | S-1 | 6 | 100 | 83 | 99 | 0.99
D12-9 | D123 | S-1 | 6 | 100 | 104 | 100 | 1
D12-10 | D121 | S-4 | 12 | 400 | 387 | 401 | 1.0025
SUPPLY |  |  |  | 1650 |  | 1648 | 0.99879
RD12-1 | D113 | R-1 | 6 | 100 | 97 | 96 | 0.96
RD12-2 | D116 | R-4 | 12 |  | 1559 | 1552 | #DIV/0! | DELETED FROM NEW DRAWING
RD12-3 | D117 | R-4 | 12 |  |  |  | #DIV/0! | DELETED FROM NEW DRAWING
RETURN |  |  |  | 100 |  | 1648 | 16.48

## HP D1-3
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP D1-3 |  | Area: D111
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 2000 | 1680
Serial Num | 224411472 |  |  |  | Fan Speed | - | 2000
[5 empty] | RA CFM | 1600 | 1680
Motor Data |  |  |  |  | RL Voltage | 460 | 482/480/481
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 3.4/3.3/3.5
Horsepower | 1 |  |  |  | Suction ESP | - | -0.96"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.08"
Phase | 3 |  |  |  | Total ESP | 0.6 | 1.04"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.28
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
D13-1 | D107 | S-1 | 6 | 50 | 94 | 41 | 0.82
D13-2 | D108 | S-1 | 6 | 50 | 93 | 41 | 0.82
D13-3 | D100 | S-4 | 12 | 550 | 422 | 456 | 0.82909
D13-4 | D001 | S-3 | 10 | 300 | 351 | 270 | 0.9
D13-5 | D101 | S-4 | 12 | 500 | 401 | 415 | 0.83
D13-6 | D100 | S-4 | 12 | 550 | 456 | 457 | 0.83091
SUPPLY |  |  |  | 2000 |  | 1680 | 0.84
RD13-1 | D100 | R-6 | 16 | 1100 | 1066 | 1135 | 1.0318
RD13-2 | D100 | R-4 | 12 | 500 | 557 | 545 | 1.09
RETURN |  |  |  | 1600 |  | 1680 | 1.05
NOTES: | HP DESIGNED FOR 1600 CFM, SGRD TOTAL IS 2000 CFM

## HP D1-4A
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP D1-4A |  | Area: D103
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TL-240 |  |  |  | SA CFM | 8000 | 8176
Serial Num | 230411901 |  |  |  | Fan Speed | - | 911
[5 empty] | RA CFM | 8000 | 8176
Motor Data |  |  |  |  | RL Voltage | 460 | 470/474/474
Motor MFG | BALDOR |  |  |  | RL Amperage | 7 | 6.3/6.4/6.7
Horsepower | 5 |  |  |  | Suction ESP | - | -0.67"
Motor Rpm | 1750 |  |  |  | Discharge ESP | - | 0.12"
Phase | 3 |  |  |  | Total ESP | 1.25 | 0.79"
Voltage (rated) | 460 |  |  |  | Brake HP | 3.98 | 4.92
Amperage (rated) | 7
[5 empty] | VHP-240 | 60 GPM
Drive Data
Motor Sheave Size / Bore |  | 1VP60 | 1.125"
Fan Sheave Size / Bore |  | BK95H | 1.1875"
Belt CL Distance |  | 30.5"
No. Belts / Size |  | 1 | BX82
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
D14A-1 | D106 | S-13 | 72X12 | 100 |  |  | 0
D14A-2 | D102 | S-11 | 24X8 | 1000 |  |  | 0
D14A-3 | D102 | S-11 | 24X8 | 950 |  |  | 0
D14A-4 | D102 | S-11 | 24X8 | 1000 |  |  | 0
D14A-5 | D102 | S-11 | 24X8 | 1000 |  |  | 0
D14A-6 | D102 | S-11 | 24X8 | 1000 |  |  | 0
D14A-7 | D102 | S-11 | 24X8 | 950 |  |  | 0
D14A-8 | D102 | S-11 | 24X8 | 1000 |  |  | 0
D14A-9 | D102 | S-11 | 24X8 | 1000 |  | 8176 | 8.176
SUPPLY |  |  |  | 8000 | TRAVERSE | 8176 | 1.022
RD14A-1 | D106 | R-11 | 8X6 | 100 |  | 102 | 1.02
RD14A-2 | D102 | R-8 | 28X40 | 3950 |  | 4037 | 1.022
RD14A-3 | D102 | R-8 | 28X40 | 3950 |  | 4037 | 1.022
RETURN |  |  |  | 8000 |  | 8176 | 1.022

## HP D1-4B
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP D1-4B |  | Area: D114
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TL-240 |  |  |  | SA CFM | 8050 | 8093 | NEW SA CFM TOTAL
Serial Num | 230510385 |  |  |  | Fan Speed | - | 902
[5 empty] | RA CFM | 8900
Motor Data |  |  |  |  | RL Voltage | 460 | 475/480/478
Motor MFG | BALDOR |  |  |  | RL Amperage | 7 | 6.4/6.4/6.2
Horsepower | 5 |  |  |  | Suction ESP | - | -0.63"
Motor Rpm | 894 |  |  |  | Discharge ESP | - | 0.23"
Phase | 3 |  |  |  | Total ESP | 1.25 | 0.86"
Voltage (rated) | 460 |  |  |  | Brake HP | 3.98 | 4.87
Amperage (rated) | 7
[5 empty] | VHP-240 | 60 GPM
Drive Data
Motor Sheave Size / Bore |  | 1VP60 | 1.125"
Fan Sheave Size / Bore |  | BK95H | 1.1875"
Belt CL Distance |  | 30.5"
No. Belts / Size |  | 1 | BX81
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
D14B-1 | D126 | S-1 | 6 | 50 |  | 50 | 1
D14B-2 | D130 | S-13 | 8X6 | 100 |  |  | 0
D14B-3 | D102 | S-11 | 24X8 | 1000 |  |  | 0
D14B-4 | D102 | S-11 | 24X8 | 950 |  |  | 0
D14B-5 | D102 | S-11 | 24X8 | 1000 |  |  | 0
D14B-6 | D102 | S-11 | 24X8 | 1000 |  |  | 0 | CHANGE CFM FROM 975 TO 1000
D14B-7 | D102 | S-11 | 24X8 | 1000 |  |  | 0 | CHANGE CFM FROM 975 TO 1000
D14B-8 | D102 | S-11 | 24X8 | 950 |  |  | 0
D14B-9 | D102 | S-11 | 24X8 | 1000 |  |  | 0
D14B-10 | D102 | S-11 | 24X8 | 1000 |  | 8043 | 8.043
SUPPLY |  |  |  | 8050 | TRAVERSE | 8093 | 1.0053
DAMPER | D129 |  |  | 900 | 856 | 856 | 0.95111
DAMPER |  |  |  | 900 |  | 856 | 0.95111
RD14B-1 | D130 | R-11 | 8X6 | 100 |  |  | 0
RD14B-2 | D102 | R-8 | 28X40 | 4400 |  |  | 0
RD14B-3 | D102 | R-8 | 28X40 | 4400 |  |  | 0
RETURN |  |  |  | 8900 |  | 0 | 0
NOTES: | 900 CFM RA VIA DAMPER BETWEEN HP 1-4B AND D1-5 RA DUCTS.

## HP D1-5
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP D1-5 |  | Area: D114
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1600 | 1643
Serial Num | 221311342 |  |  |  | Fan Speed | - | 1600
[5 empty] | RA CFM | 900 | 787
Motor Data |  |  |  |  | RL Voltage | 460 | 466/468/470
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 3.0/3.0/3.0
Horsepower | 1 |  |  |  | Suction ESP | - | -0.57"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.25"
Phase | 3 |  |  |  | Total ESP | 0.6 | 0.82"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.25
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
D15-1 | D135 | S-4 | 12 | 400 | 440 | 402 | 1.005
D15-2 | D131 | S-1 | 6 | 75 | 0 | 79 | 1.0533
D15-3 | D136 | S-1 | 6 | 50 | 83 | 51 | 1.02
D15-4 | D137 | S-1 | 6 | 50 | 84 | 52 | 1.04
D15-5 | D132 | S-1 | 6 | 75 | 0 | 78 | 1.04
D15-6 | D128 | S-4 | 12 | 400 | 486 | 410 | 1.025
D15-7 | D125 | S-2 | 8 | 200 | 165 | 208 | 1.04
D15-8 | D133 | S-1 | 6 | 75 | 0 | 80 | 1.0667
D15-9 | D138 | S-3 | 10 | 275 | 283 | 283 | 1.0291
SUPPLY |  |  |  | 1600 |  | 1643 | 1.0269
DAMPER | D129 |  |  | 900 |  | 856 | 0.95111
DAMPER |  |  |  | 900 |  | 856 | 0.95111
RD15-1 | D125 | R-2 | 8 | 200 | 230 | 195 | 0.975
RD15-2 | D131 | R-1 | 6 | 75 | 85 | 72 | 0.96
RD15-3 | D132 | R-1 | 6 | 75 | 86 | 71 | 0.94667
RD15-4 | D133 | R-1 | 6 | 75 | 60 | 69 | 0.92
|  |  |  | 200 | 114 | 165 | 0.825
RD15-5 | D138 | R-3 | 10 | 275 | 293 | 215 | 0.78182
RETURN |  |  |  | 900 |  | 787 | 0.87444
NOTES: | 900 CFM RA VIA DAMPER BETWEEN HP 1-4B AND D1-5 RA DUCTS.

## HP E1-1
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP E1-1 |  | Area: D103
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-038 |  |  |  | SA CFM | 1200 | 1208
Serial Num | 224611425 |  |  |  | Fan Speed | - | 1225
[5 empty] | RA CFM | 1100 | 1082 | NEW RA CFM TOTAL
Motor Data |  |  |  |  | RL Voltage | 460 | 488/485/488
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 3.2 | 1.5/1.7/1.6
Horsepower | 0.5 |  |  |  | Suction ESP | - | -0.58"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.08"
Phase | 3 |  |  |  | Total ESP | 0.6 | 0.64"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.08
Amperage (rated) | 3.2
[5 empty] | VHP-036 | 9 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
E11-1 | E101 | S-1 | 6 | 50 | 84 | 51 | 1.02
E11-2 | E100 | S-2 | 8 | 200 | 180 | 196 | 0.98
E11-3 | E105 | S-3 | 10 | 250 | 306 | 261 | 1.044
E11-4 | E105 | S-3 | 10 | 300 | 42 | 302 | 1.0067
E11-5 | E105 | S-1 | 6 | 100 | 81 | 95 | 0.95
E11-6 | E105 | S-3 | 10 | 250 | 301 | 251 | 1.004
E11-7 | E107 | S-1 | 6 | 50 | 128 | 52 | 1.04
SUPPLY |  |  |  | 1200 |  | 1208 | 1.0067
RE11-1 | E105 | R-6 |  | 1100 | 1082 | 1082 | 0.98364 | CHANGED CFM FROM 500 TO 1100
RETURN |  |  |  | 1100 |  | 1082 | 0.98364

## HP E1-2
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP E1-2 |  | Area: D103
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-026 |  |  |  | SA CFM | 800 | 831
Serial Num | 224610910 |  |  |  | Fan Speed | - | 750
[5 empty] | RA CFM | 800 | 831
Motor Data |  |  |  |  | RL Voltage | 265 | 286
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 3.2 | 0.7
Horsepower | 0.5 |  |  |  | Suction ESP |  | -0.16"
Motor Rpm | NL |  |  |  | Discharge ESP |  | 0.02
Phase | 1 |  |  |  | Total ESP | 0.6 | 0.18"
Voltage (rated) | 265 |  |  |  | Brake HP |  | 0.10937
Amperage (rated) | 3.2
[5 empty] | VHP-024 | 6 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
E12-1 | E106 | S-3 | 10 | 250 | 350 | 251 | 1.004
E12-2 | E109 | S-1 | 6 | 50 | 112 | 71 | 1.42
E12-3 | E106 | S-3 | 10 | 250 | 0 | 253 | 1.012
E12-4 | E106 | S-3 | 10 | 250 | 340 | 256 | 1.024
SUPPLY |  |  |  | 800 |  | 831 | 1.0388
RE12-1 | E106 | R-5 | 14 | 800 | 735 | 831 | 1.0388
RETURN |  |  |  | 800 |  | 831 | 1.0388

## HP E1-3
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP E1-3 |  | Area: D103
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-009 |  |  |  | SA CFM | 300 | 366
Serial Num | 224411025 |  |  |  | Fan Speed | - | LOW
[5 empty] | RA CFM | 400 | 256
Motor Data |  |  |  |  | RL Voltage | 265 | 284
Motor MFG | US MOTORS |  |  |  | RL Amperage | 0.4 | 0.3
Horsepower | 0.05 |  |  |  | Suction ESP | - | -0.12"
Motor Rpm | 1580 |  |  |  | Discharge ESP | - | 0.04"
Phase | 1 |  |  |  | Total ESP | 0.7 | 0.16"
Voltage (rated) | 265 |  |  |  | Brake HP | - | 0.003
Amperage (rated) | 0.4
[5 empty] | VHP-009 | 1.88 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
E13-1 | E104 | S-1 | 6 | 75 | 93 | 93 | 1.24
E13-2 | E111 | S-1 | 6 | 75 | 94 | 94 | 1.2533
E13-3 | E112 | S-2 | 8 | 150 | 177 | 177 | 1.18
SUPPLY |  |  |  | 300 |  | 364 | 1.2133
RE13-1 | E104 | R-1 | 6 | 100 | 61 | 61 | 0.61
RE13-2 | E111 | R-1 | 6 | 100 | 61 | 61 | 0.61
RE13-3 | E112 | R-2 | 8 | 200 | 134 | 134 | 0.67
RETURN |  |  |  | 400 |  | 256 | 0.64
NOTES: | HP DESIGNED FOR 230 CFM, SGRD TOTAL IS 300, EGRD TOTAL IS 400

## HP E1-4
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP E1-4 |  | Area: D103
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-012 |  |  |  | SA CFM | 350 | 348
Serial Num | 2243105541 |  |  |  | Fan Speed | - | LOW
[5 empty] | RA CFM | 350
Motor Data |  |  |  |  | RL Voltage | 265 | 280
Motor MFG | US MOTORS |  |  |  | RL Amperage | 0.7 | 0.4
Horsepower | 0.14 |  |  |  | Suction ESP | - | -0.15"
Motor Rpm | 1625 |  |  |  | Discharge ESP | - | 0.10"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.25
Voltage (rated) | 265 |  |  |  | Brake HP | - | 0.01
Amperage (rated) | 0.7
[5 empty] | VHP-012 | 2.5 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
E14-1 | E110 | S-1 | 6 | 50 | 51 | 51 | 1.02
E14-2 | E122 | S-3 | 10 | 300 | 297 | 297 | 0.99
SUPPLY |  |  |  | 350 |  | 348 | 0.99429
RE14-1 | E110 | R-1 | 6 | 50 | 85 | 46 | 0.92
RE14-2 | E122 | R-3 | 10 | 300 | 215 | 264 | 0.88
RETURN |  |  |  | 350 |  | 310 | 0.88571

## HP E1-5
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP E1-5 |  | Area: D103
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-026 |  |  |  | SA CFM | 700 | 728
Serial Num | 224610909 |  |  |  | Fan Speed | - | 675
[5 empty] | RA CFM | 700 | 728
Motor Data |  |  |  |  | RL Voltage | 265 | 288
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 3.2 | 0.8
Horsepower | 0.5 |  |  |  | Suction ESP | - | -0.31"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.08"
Phase | 1 |  |  |  | Total ESP | 0.6 | 0.39"
Voltage (rated) | 265 |  |  |  | Brake HP | - | 0.03
Amperage (rated) | 3.2
[5 empty] | VHP-024 | 6 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
E15-1 | E116 | S-1 | 6 | 50 | 0 | 54 | 1.08
E15-2 | E118 | S-2 | 8 | 200 | 261 | 208 | 1.04
E15-3 | E118 | S-2 | 8 | 200 | 257 | 206 | 1.03
E15-4 | E118 | S-2 | 8 | 200 | 0 | 207 | 1.035
E15-5 | E117 | S-1 | 6 | 50 | 144 | 53 | 1.06
SUPPLY |  |  |  | 700 |  | 728 | 1.04
RE15-1 | E116 | R-1 | 6 | 50 | 0 | 42 | 0.84
RE15-2 | E117 | R-1 | 6 | 50 | 442 | 45 | 0.9
RE15-3 | E118 | R-4 | 12 | 600 | 220 | 641 | 1.0683
RETURN |  |  |  | 700 |  | 728 | 1.04

## HP E1-6
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP E1-6 |  | Area: D103
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-026 |  |  |  | SA CFM | 800 | 819
Serial Num | 224610404 |  |  |  | Fan Speed | - | 775
[5 empty] | RA CFM | 1200 | 819
Motor Data |  |  |  |  | RL Voltage | 265 | 264
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 3.2 | 1.4
Horsepower | 0.5 |  |  |  | Suction ESP | - | -0.71"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.05"
Phase | 1 |  |  |  | Total ESP | 0.6 | 0.81"
Voltage (rated) | 265 |  |  |  | Brake HP | - | 0.06
Amperage (rated) | 3.2
[5 empty] | VHP-024 | 6 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
E16-1 | E113 | S-3 | 10 | 275 | 328 | 283 | 1.0291
E16-2 | E113 | S-3 | 10 | 250 | 330 | 255 | 1.02
E16-3 | E113 | S-3 | 10 | 275 | 331 | 281 | 1.0218
SUPPLY |  |  |  | 800 |  | 819 | 1.0237
RE16-1 | E113 | R-12 | 24X10 | 800 | 989 | 819 | 1.0237
RETURN |  |  |  | 800 |  | 819 | 1.0237
NOTES:

## HP E1-7
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP E1-7 |  | Area: E119
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-026 |  |  |  | SA CFM | 800 | 830 | NEW SA CFM TOTAL
Serial Num | 224610903 |  |  |  | Fan Speed | - | 750
[5 empty] | RA CFM | 800 | 830
Motor Data |  |  |  |  | RL Voltage | 265 | 277
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 3.2 | 0.8
Horsepower | 0.5 |  |  |  | Suction ESP | - | -0.25"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.08"
Phase | 1 |  |  |  | Total ESP | 0.6 | 0.41"
Voltage (rated) | 265 |  |  |  | Brake HP | - | 0.03
Amperage (rated) | 3.2
[5 empty] | VHP-024 | 6 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
E17-1 | E115 | S-3 | 10 | 250 | 377 | 255 | 1.02 | CHANGE CFM FROM 400 TO 250
E17-2 | E115 | S-3 | 10 | 275 | 321 | 285 | 1.0364 | CHANGE CFM FROM 400 TO 275
E17-3 | E115 | S-3 | 10 | 275 | 312 | 290 | 1.0545 | CHANGE CFM FROM 350 TO 275
SUPPLY |  |  |  | 800 |  | 830 | 1.0375
RE17-1 | E115 | R-5 | 14 | 800 | 1010 | 830 | 1.0375
RETURN |  |  |  | 800 |  | 830 | 1.0375
NOTES:

## HP E1-8A
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP E1-8A |  | Area: E137
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-72 |  |  |  | SA CFM | 2400
Serial Num |  |  |  |  | Fan Speed
[5 empty] | RA CFM | 2400
Motor Data |  |  |  |  | RL Voltage | 460
Motor MFG |  |  |  |  | RL Amperage | 6
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 0.6
Voltage (rated) | 460 |  |  |  | Brake HP
Amperage (rated) | 6
[5 empty] | VHP-072 | 17 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
E18-1 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-2 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-3 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-4 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-5 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-6 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-7 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-8 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-9 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-10 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-11 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-12 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-13 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-14 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-15 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-16 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-17 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-18 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-19 | E121 | S-7 | 20X8 | 240 |  |  | 0
E18-20 | E121 | S-7 | 20X8 | 240 |  |  | 0
SUPPLY |  |  |  | 4800 |  | 0 | 0
RE18-1 | E121 | R-10 |  | 4800 |  |  | 0
RETURN |  |  |  | 4800 |  | 0 | 0
NOTES: | E1-8A AND E1-8B SHARE COMMON SUPPLY AND RETURN DUCTS. ALL GRD'S LISTED ON E1-18A.
HP DESIGN IS 2300 CFM, SGRD TOTAL IS 4800 CFM (2400/HP), EGRD TOTAL IS 4800 CFM (2400 CFM/HP)

## HP E1-8B
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP E1-8B |  | Area: E137
Unit Data |  |  | Test Data
MFG | CLIMATEMASTER |  |  | Design | Actual
Model Num | TE-72 |  | SA CFM | 2400
Serial Num |  |  | Fan Speed
|  |  | RA CFM | 2400
Motor Data |  |  | RL Voltage | 460
Motor MFG |  |  | RL Amperage | 6
Horsepower |  |  | Suction ESP
Motor Rpm |  |  | Discharge ESP
Phase | 3 |  | Total ESP | 0.6
Voltage (rated) | 460 |  | Brake HP
Amperage (rated) | 6
|  |  | VHP-072 | 17 GPM
NOTES: | E1-8A AND E1-8B SHARE COMMON SUPPLY AND RETURN DUCTS. ALL GRD'S LISTED ON E1-18A.
HP DESIGN IS 2300 CFM, SGRD TOTAL IS 4800 CFM (2400/HP), EGRD TOTAL IS 4800 CFM (2400 CFM/HP)

## HP E1-9
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP E1-9 |  | Area: E131
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-018 |  |  |  | SA CFM | 800 |  | NEW SA CFM TOTAL
Serial Num |  |  |  |  | Fan Speed
[5 empty] | RA CFM | 650 |  | NEW RA CFM TOTAL
Motor Data |  |  |  |  | RL Voltage | 265
Motor MFG |  |  |  |  | RL Amperage | 0.9
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP | 0.4
Voltage (rated) | 265 |  |  |  | Brake HP
Amperage (rated) | 0.9
[5 empty] | VHP-018 | 3.75 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
E19-1 | E132 | S-2 | 8 | 150 |  |  | 0
E19-2 | E127 | S-2 | 8 | 150 |  |  | 0
E19-3 | E127 | S-2 | 8 | 150 |  |  | 0
E19-4 | E127 | S-2 | 8 | 175 |  |  | 0 | CHANGE CFM FROM 150 TO 175
E19-5 | E127 | S-2 | 8 | 175 |  |  | 0 | CHANGE CFM FROM 150 TO 175
SUPPLY |  |  |  | 800 |  | 0 | 0
RE19-1 | E127 | R-5 | 14 | 650 |  |  | 0 | CHANGE CFM FROM 800 TO 650
RE19-2 | [7 empty] | DELETE RE19-2
RETURN |  |  |  | 650 |  | 0 | 0
NOTES: | HP DESIGN IS 573 CFM, SGRD TOTAL IS 800 CFM, EGRD TOTAL IS 650 CFM

## HP E1-10
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP E1-10 |  | Area: E131
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-064 |  |  |  | SA CFM | 1800
Serial Num |  |  |  |  | Fan Speed
[5 empty] | RA CFM | 2400
Motor Data |  |  |  |  | RL Voltage | 460
Motor MFG |  |  |  |  | RL Amperage | 6
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 0.6
Voltage (rated) | 460 |  |  |  | Brake HP
Amperage (rated) | 6
[5 empty] | VHP-060 | 15 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
E110-1 | E128 | S-2 | 8 | 275 |  |  | 0
E110-2 | E129 | S-1 | 6 | 75 |  |  | 0
E110-3 | E134 | S-1 | 6 | 75 |  |  | 0
E110-4 | E125 | S-1 | 6 | 75 |  |  | 0
E110-5 | E128 | S-2 | 8 | 275 |  |  | 0
E110-6 | E128 | S-2 | 8 | 275 |  |  | 0
E110-7 | E128 | S-2 | 8 | 275 |  |  | 0
E110-8 | E128 | S-2 | 8 | 275 |  |  | 0
E110-9 | E128 | S-2 | 8 | 200 |  |  | 0
SUPPLY |  |  |  | 1800 |  | 0 | 0
RE110-1 | E128 | R-5 | 14 | 800 |  |  | 0
RE110-1 | E128 | R-5 | 14 | 800 |  |  | 0
RE110-1 | E128 | R-5 | 14 | 800 |  |  | 0
RETURN |  |  |  | 2400 |  | 0 | 0
NOTES: | HP DESIGN IS 2000 CFM, SGRD TOTAL IS 1800 CFM, EGRD TOTAL IS 2400 CFM

## HP F1-1
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP F1-1 |  | Area: F103
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-038 |  |  |  | SA CFM | 1100 | 1133 | NEW SA CFM TOTAL
Serial Num | 224511536 |  |  |  | Fan Speed | - | 1200
[5 empty] | OA CFM | 100 |  | NEW OA CFM TOTAL
[5 empty] | RA CFM | 1000 | 1029 | NEW RA CFM TOTAL
Motor Data |  |  |  |  | RL Voltage | 460 | 487/486/483
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 3.2 | 1.8/1.7/1.8
Horsepower | 0.5 |  |  |  | Suction ESP | - | 0.58"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.13"
Phase | 3 |  |  |  | Total ESP | 0.6 | 0.71"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.1
Amperage (rated) | 3.2
[5 empty] | VHP-036 | 9 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F11-1 | F101 | S-1 | 6 | 50 | 57 | 52 | 1.04
F11-2 | F100 | S-1 | 6 | 50 | 56 | 55 | 1.1
F11-4 | F104 | S-3 | 10 | 300 | 341 | 306 | 1.02
F11-5 | F104 | S-3 | 10 | 350 | 375 | 359 | 1.0257
F11-6 | F104 | S-3 | 10 | 350 | 375 | 361 | 1.0314
SUPPLY |  |  |  | 1100 |  | 1133 | 1.03
RF11-1 | E120 | R-2 | 8 | 300 | 250 | 250 | 0.83333
RF11-2 | F104 | R-5 | 14 | 800 | 779 | 779 | 0.97375 | CHANGE CFM FROM 1000 TO 800
RETURN |  |  |  | 1100 |  | 1029 | 0.93545

## HP F1-2
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP F1-2 |  | Area: F106
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1600 | 1615
Serial Num | 224611430 |  |  |  | Fan Speed | - | 1475
[5 empty] | RA CFM | 1600 | 1615
Motor Data |  |  |  |  | RL Voltage | 460 | 493/493/489
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 1.8/1.8/1.7
Horsepower | 1 |  |  |  | Suction ESP | - | -0.45"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.04"
Phase | 3 |  |  |  | Total ESP | 0.6 | 0.49"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.15
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F12-1 | F107 | S-3 | 10 | 250 | 395 | 255 | 1.02
F12-2 | F107 | S-3 | 10 | 275 | 0 | 276 | 1.0036
F12-3 | F107 | S-3 | 10 | 275 | 0 | 275 | 1
F12-4 | F105 | S-3 | 10 | 250 | 475 | 256 | 1.024
F12-5 | F105 | S-3 | 10 | 275 | 387 | 276 | 1.0036
F12-6 | F105 | S-3 | 10 | 275 | 394 | 277 | 1.0073
SUPPLY |  |  |  | 1600 |  | 1615 | 1.0094
RF12-1 | F105 | R-5 | 14 | 800 | 1034 | 809 | 1.0112
RF12-2 | F107 | R-5 | 14 | 800 | 617 | 806 | 1.0075
RETURN |  |  |  | 1600 |  | 1615 | 1.0094

## HP F1-3
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP F1-3 |  | Area: F112
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1600 | 1645
Serial Num | 224611428 |  |  |  | Fan Speed | - | 1525
[5 empty] | RA CFM | 1600 | 1480
Motor Data |  |  |  |  | RL Voltage | 460 | 488/485/488
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 21/2.2/2.1
Horsepower | 1 |  |  |  | Suction ESP | - | -0.61"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.05"
Phase | 3 |  |  |  | Total ESP | 0.6 | 0.66"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.17
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F13-1 | F111 | S-3 | 10 | 250 | 360 | 261 | 1.044
F13-2 | F111 | S-3 | 10 | 250 | 94 | 256 | 1.024
F13-3 | F111 | S-3 | 10 | 250 | 272 | 251 | 1.004
F13-4 | F113 | S-3 | 10 | 250 | 76 | 261 | 1.044
F13-5 | F113 | S-3 | 10 | 250 | 246 | 258 | 1.032
F13-6 | F113 | S-3 | 10 | 250 | 274 | 257 | 1.028
F13-7 | F114 | S-1 | 6 | 100 | 61 | 101 | 1.01
SUPPLY |  |  |  | 1600 |  | 1645 | 1.0281
RF13-1 | F113 | R-5 | 14 | 800 | 76 | 740 | 0.925
RF13-2 | F111 | R-5 | 14 | 800 | 1012 | 740 | 0.925
RETURN |  |  |  | 1600 |  | 1480 | 0.925

## HP F1-4
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP F1-4 |  | Area: F109
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1600 | 1621
Serial Num | 224611431 |  |  |  | Fan Speed | - | 1475
[5 empty] | RA CFM | 1600 | 1466
Motor Data |  |  |  |  | RL Voltage | 460 | 492/492/488
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 2.1/2.1/1.9
Horsepower | 1 |  |  |  | Suction ESP | - | -0.65"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.05"
Phase | 3 |  |  |  | Total ESP | 0.6 | 0.70"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.17
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
F14-1 | F108 | S-3 | 10 | 250 | 461 | 261 | 1.044
F14-2 | F108 | S-3 | 10 | 275 | 351 | 279 | 1.0145
F14-3 | F108 | S-3 | 10 | 275 | 432 | 276 | 1.0036
F14-4 | F110 | S-3 | 10 | 250 | 273 | 251 | 1.004
F14-5 | F110 | S-3 | 10 | 275 | 54 | 276 | 1.0036
F14-6 | F110 | S-3 | 10 | 275 | 55 | 278 | 1.0109
SUPPLY |  |  |  | 1600 |  | 1621 | 1.0131
RF14-1 | F110 | R-5 | 14 | 800 | 615 | 733 | 0.91625
RF14-2 | F108 | R-5 | 14 | 800 | 852 | 733 | 0.91625
RETURN |  |  |  | 1600 |  | 1466 | 0.91625

## HP C2-1
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP C2-1 |  | Area: C203
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-038 |  |  |  | SA CFM | 1200
Serial Num |  |  |  |  | Fan Speed
[5 empty] | RA CFM | 1200
Motor Data |  |  |  |  | RL Voltage | 460
Motor MFG |  |  |  |  | RL Amperage | 3.2
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 3 |  |  |  | Total ESP | 0.6
Voltage (rated) | 460 |  |  |  | Brake HP
Amperage (rated) | 3.2
[5 empty] | VHP-036 | 9 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C21-1 | SA200 | S-6 | 12X8 | 300 |  |  | 0
C21-2 | C202 | S-1 | 6 | 100 |  |  | 0
C21-3 | C205 | S-3 | 10 | 275 |  |  | 0
C21-4 | C205 | S-3 | 10 | 275 |  |  | 0
C21-5 | C205 | S-3 | 10 | 250 |  |  | 0
SUPPLY |  |  |  | 1200 |  | 0 | 0
RC21-1 | C202 | R-1 | 6 | 100 |  |  | 0
RC21-2 | SA200 | R-7 | 12X6 | 300 |  |  | 0
RC21-3 | C205 | R-5 | 14 | 800 |  |  | 0
RETURN |  |  |  | 1200 |  | 0 | 0

## HP C2-2
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP C2-1 |  | Area: C203
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-018 |  |  |  | SA CFM | 600 | 678
Serial Num | 224310549 |  |  |  | Fan Speed | - | LOW
[5 empty] | RA CFM | 600 | 678
Motor Data |  |  |  |  | RL Voltage | 265 | 275
Motor MFG | US MOTORS |  |  |  | RL Amperage | 0.9 | 0.6
Horsepower | 0.125 |  |  |  | Suction ESP | - | -0.23"
Motor Rpm | 1020 |  |  |  | Discharge ESP | - | 0.14"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.37"
Voltage (rated) | 265 |  |  |  | Brake HP | - | 0.01
Amperage (rated) | 0.9
[5 empty] | VHP-018 | 3.75 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C22-1 | C204 | S-3 | 10 | 300 | 367 | 340 | 1.1333
C22-2 | C204 | S-3 | 10 | 300 | 345 | 338 | 1.1267
SUPPLY |  |  |  | 600 |  | 678 | 1.13
RC22-1 | C204 | R-4 | 12 | 600 | 713 | 678 | 1.13
RETURN |  |  |  | 600 |  | 678 | 1.13
NOTES: | HP DESIGN IS 573 CFM, SGRD TOTAL IS 600 CFM, EGRD TOTAL IS 600 CFM

## HP C2-3
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP C2-3 |  | Area: C207
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1600 | 1638
Serial Num | 224611435 |  |  |  | Fan Speed | - | 1500
[5 empty] | RA CFM | 1600 | 1444
Motor Data |  |  |  |  | RL Voltage | 460 | 475/470/475
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 1.8/1.6/1.8
Horsepower | 1 |  |  |  | Suction ESP | - | -0.35"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.05"
Phase | 3 |  |  |  | Total ESP | 0.6 | 0.40"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.14
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C23-1 | C206 | S-3 | 10 | 250 | 308 | 255 | 1.02
C23-2 | C206 | S-3 | 10 | 275 | 288 | 278 | 1.0109
C23-3 | C206 | S-3 | 10 | 275 | 267 | 283 | 1.0291
C23-4 | C208 | S-3 | 10 | 250 | 344 | 260 | 1.04
C23-5 | C208 | S-3 | 10 | 275 | 275 | 282 | 1.0255
C23-6 | C208 | S-3 | 10 | 275 | 284 | 281 | 1.0218
SUPPLY |  |  |  | 1600 |  | 1639 | 1.0244
RC23-1 | C206 | R-5 | 14 | 800 | 690 | 722 | 0.9025
RC23-2 | C208 | R-5 | 14 | 800 | 752 | 722 | 0.9025
RETURN |  |  |  | 1600 |  | 1444 | 0.9025

## HP C2-4
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP C2-4 |  | Area: C210
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1600 | 1646
Serial Num | 224611437 |  |  |  | Fan Speed | - | 1550
[5 empty] | RA CFM | 1600 | 1515
Motor Data |  |  |  |  | RL Voltage | 460 | 470/466/470
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 1.9/1.7/1.9
Horsepower | 1 |  |  |  | Suction ESP | - | -0.35"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.08"
Phase | 3 |  |  |  | Total ESP | 0.6 | 0.43"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.15
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C24-1 | C209 | S-3 | 10 | 250 | 46 | 261 | 1.044
C24-2 | C209 | S-3 | 10 | 275 | 49 | 279 | 1.0145
C24-3 | C209 | S-3 | 10 | 275 | 366 | 281 | 1.0218
C24-4 | C211 | S-3 | 10 | 250 | 386 | 261 | 1.044
C24-5 | C211 | S-3 | 10 | 275 | 343 | 283 | 1.0291
C24-6 | C211 | S-3 | 10 | 275 | 415 | 281 | 1.0218
SUPPLY |  |  |  | 1600 |  | 1646 | 1.0288
RC24-1 | C209 | R-5 | 14 | 800 | 700 | 754 | 0.9425
RC24-2 | C211 | R-5 | 14 | 800 | 815 | 761 | 0.95125
RETURN |  |  |  | 1600 |  | 1515 | 0.94688

## HP C2-5
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP C2-5 |  | Area: C231
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-012 |  |  |  | SA CFM | 300 | 361
Serial Num | 224310539 |  |  |  | Fan Speed | - | LOW
[5 empty] | RA CFM | 300 | 311
Motor Data |  |  |  |  | RL Voltage | 265 | 274
Motor MFG | US MOTORS |  |  |  | RL Amperage | 0.7 | 0.4
Horsepower | 0.14 |  |  |  | Suction ESP | - | -0.23"
Motor Rpm | 1625 |  |  |  | Discharge ESP | - | 0.15"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.38"
Voltage (rated) | 265 |  |  |  | Brake HP | - | 0.01
Amperage (rated) | 0.7
[5 empty] | VHP-012 | 2.5 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C25-1 | C228 | S-1 | 6 | 50 | 96 | 60 | 1.2
C25-2 | C227 | S-1 | 6 | 50 | 108 | 62 | 1.24
C25-3 | C219 | S-1 | 6 | 100 | 89 | 118 | 1.18
C25-4 | C232 | S-2 | 8 | 100 | 145 | 121 | 1.21
SUPPLY |  |  |  | 300 |  | 361 | 1.2033
RC25-1 | C219 | R-1 | 6 | 100 | 130 | 102 | 1.02
RC25-2 | C232 | R-1 | 6 | 200 | 240 | 209 | 1.045
RETURN |  |  |  | 300 |  | 311 | 1.0367

## HP C2-6
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP C2-6 |  | Area: C231
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-012 |  |  |  | SA CFM | 400 | 402
Serial Num | 224310538 |  |  |  | Fan Speed | - | LOW
[5 empty] | RA CFM | 400 | 402
Motor Data |  |  |  |  | RL Voltage | 265 | 273
Motor MFG | US MOTORS |  |  |  | RL Amperage | 0.7 | 0.3
Horsepower | 0.14 |  |  |  | Suction ESP | - | -0.08"
Motor Rpm | 1625 |  |  |  | Discharge ESP | - | 0.03"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.11"
Voltage (rated) | 265 |  |  |  | Brake HP | - | 0.01
Amperage (rated) | 0.7
[5 empty] | VHP-012 | 2.5 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C26-1 | C223 | S-4 | 12 | 400 | 480 | 402 | 1.005
SUPPLY |  |  |  | 400 |  | 402 | 1.005
RC26-1 | C223 | R-4 | 12 | 400 | 480 | 402 | 1.005
RETURN |  |  |  | 400 |  | 402 | 1.005

## HP C2-7
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP C2-7 |  | Area: C218
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1600 | 1640 | NEW SA CFM TOTAL
Serial Num | 224611440 |  |  |  | Fan Speed | - | 1500
[5 empty] | RA CFM | 1800 | 1470
Motor Data |  |  |  |  | RL Voltage | 460 | 478/470/473
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 1.9/1.7/1.9
Horsepower | 1 |  |  |  | Suction ESP | - | -0.39"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.06"
Phase | 3 |  |  |  | Total ESP | 0.6 | 0.45"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.15
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C27-1 | C217 | S-2 | 8 | 200 | 286 | 203 | 1.015 | CHANGE CFM FROM 225 TO 200
C27-2 | C221 | S-2 | 8 | 150 | 168 | 156 | 1.04
C27-3 | C217 | S-3 | 10 | 250 | 273 | 256 | 1.024
C27-4 | C217 | S-3 | 10 | 250 | 264 | 255 | 1.02
C27-5 | C220 | S-1 | 6 | 50 | 114 | 52 | 1.04
C27-6 | C222 | S-2 | 8 | 200 | 227 | 209 | 1.045
C27-7 | C222 | S-3 | 10 | 250 | 167 | 257 | 1.028
C27-8 | C222 | S-3 | 10 | 250 | 288 | 252 | 1.008
SUPPLY |  |  |  | 1600 |  | 1640 | 1.025
RC27-1 | C217 | R-5 | 14 | 800 | 747 | 659 | 0.82375
RC27-2 | C220 | R-1 | 6 | 50 | 45 | 41 | 0.82
RC27-3 | C221 | R-2 | 8 | 150 | 143 | 123 | 0.82
RC27-4 | C222 | R-5 | 14 | 800 | 518 | 647 | 0.80875
RETURN |  |  |  | 1800 |  | 1470 | 0.81667
NOTES: | HP DESIGN IS 1600 CFM, SGRD TOTAL IS 1625 CFM, EGRD TOTAL IS 1800 CFM

## HP C2-8
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP C2-8 |  | Area: C215
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TE-049 |  |  |  | SA CFM | 1600 | 1668
Serial Num | 224611436 |  |  |  | Fan Speed | - | 1500
[5 empty] | RA CFM | 1600 | 1522
Motor Data |  |  |  |  | RL Voltage | 460 | 478/481/481
Motor MFG | PERFECT SPEED |  |  |  | RL Amperage | 6 | 2.2/2.1/2.1
Horsepower | 1 |  |  |  | Suction ESP | - | -0.48"
Motor Rpm | NL |  |  |  | Discharge ESP | - | 0.04"
Phase | 3 |  |  |  | Total ESP | 0.6 | 0.52"
Voltage (rated) | 460 |  |  |  | Brake HP | - | 0.2
Amperage (rated) | 6
[5 empty] | VHP-048 | 12 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C28-1 | C216 | S-3 | 10 | 250 | 304 | 263 | 1.052
C28-2 | C216 | S-3 | 10 | 275 | 287 | 283 | 1.0291
C28-3 | C216 | S-3 | 10 | 275 | 219 | 288 | 1.0473
C28-4 | C214 | S-3 | 10 | 250 | 312 | 262 | 1.048
C28-5 | C214 | S-3 | 10 | 275 | 326 | 284 | 1.0327
C28-6 | C214 | S-3 | 10 | 275 | 273 | 288 | 1.0473
SUPPLY |  |  |  | 1600 |  | 1668 | 1.0425
RC28-1 | C216 | R-5 | 14 | 800 | 786 | 761 | 0.95125
RC28-2 | C214 | R-5 | 14 | 800 | 736 | 761 | 0.95125
RETURN |  |  |  | 1600 |  | 1522 | 0.95125

## HP C2-9
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: HEAT PUMP C2-9 |  | Area: C215
Unit Data |  |  |  |  | Test Data
MFG | CLIMATEMASTER |  |  |  |  | Design | Actual
Model Num | TS-018 |  |  |  | SA CFM | 600 | 654 | NEW SA CFM TOTAL
Serial Num | 224411031 |  |  |  | Fan Speed | - | LOW
[5 empty] | OA CFM | 150
[5 empty] | RA CFM | 660 | 539 | NEW RA CFM TOTAL
Motor Data |  |  |  |  | RL Voltage | 265 | 277
Motor MFG | US MOTORS |  |  |  | RL Amperage | 0.9 | 0.5
Horsepower | 0.125 |  |  |  | Suction ESP | - | -0.18"
Motor Rpm | 1020 |  |  |  | Discharge ESP | - | 0.15"
Phase | 1 |  |  |  | Total ESP | 0.4 | 0.33"
Voltage (rated) | 265 |  |  |  | Brake HP | - | 0.09
Amperage (rated) | 0.9
[5 empty] | VHP-018 | 3.75 GPM
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
C29-1 | C113 | S-2 | 8 | 150 | 182 | 164 | 1.0933 | CHANGE CFM FROM MISSING TO 150
C29-2 | C213 | S-2 | 8 | 150 | 236 | 164 | 1.0933
C29-3 | SB200 | S-6 |  | 300 | 279 | 326 | 1.0867
SUPPLY |  |  |  | 600 |  | 654 | 1.09
RC29-1 | C113 | R-2 | 8 | 150 | 201 | 123 | 0.82 | CHANGE CFM FROM MISSING TO 150
RC29-2 | SB200 | R3 | 10 | 360 | 0 | 293 | 0.81389 | CHANGE CFM FROM 300 TO 360, TYPE, SIZE
RC29-3 | C213 | R-2 | 8 | 150 | 250 | 123 | 0.82
RETURN |  |  |  | 660 |  | 539 | 0.81667

## DOAS-1
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: DOAS-1 |  | Area: BLDG VENTILATION
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ADDISON |  | Manufacturer | ADDISON
Model Number | PROH |  | Model Number | PROH
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X20 |  | No. Pre Filters / Size
No. Pre Filters / Size | 3 / 25X25
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 10 / 2164 |  | Horsepower / RPM | 15 / 1602
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 12.4 |  | Rated Amperage / SF | 18.6
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 12500 |  | Total CFM | 11250
Min OA CFM | 12500
Fan RPM | 2164 |  | Fan RPM | 1602
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | 12.4 |  | RL Amperage | 18.6
Motor B.H.P. | 14.99 |  | Motor B.H.P. | 9.66
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 5.13 |  | Total SP | 3.02
DX Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 2.5 |  | Total ESP | 1
NOTES: | DOAS-1 AND DOAS-2 SHARE COMMON SUPPLY AND RETURN DUCTS. ALL EGRD'S LISTED ON DOAS-1&2 EGRD's SHEETS.

## DOAS-2
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: DOAS-2 |  | Area: BLDG VENTILATION
Supply Side |  |  | Return Side
Unit Data |  |  | Unit Data
Manufacturer | ADDISON |  | Manufacturer | ADDISON
Model Number | PROH |  | Model Number | PROH
Serial Number |  |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 6 / 25X20 |  | No. Pre Filters / Size
No. Pre Filters / Size | 3 / 25X25
Motor Data X |  |  | Motor Data X
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 10 / 2164 |  | Horsepower / RPM | 15 / 1602
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 12.4 |  | Rated Amperage / SF | 18.6
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 12500 |  | Total CFM | 11250
Min OA CFM | 12500
Fan RPM | 2164 |  | Fan RPM | 1602
VFD Speed |  |  | VFD Speed
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage | 12.4 |  | RL Amperage | 18.6
Motor B.H.P. | 14.99 |  | Motor B.H.P. | 9.66
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 5.13 |  | Total SP | 3.02
DX Coil P.D.
System Set Point
Pre Filters P.D.
Pre Filters P.D.
Total ESP | 2.5 |  | Total ESP | 1
NOTES: | DOAS-1 AND DOAS-2 SHARE COMMON SUPPLY AND RETURN DUCTS. ALL EGRD'S LISTED ON DOAS-1&2 EGRD's SHEETS.

## DOAS-1&2 EGRD's (1)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: DOAS-1&2 EGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
DE-1 | F113 | E-3 | 10 | 300 |  |  | 0
DE-2 | F111 | E-3 | 10 | 300 |  |  | 0
DE-3 | F104 | E-3 | 10 | 300 |  |  | 0
DE-4 | F105 | E-3 | 10 | 300 |  |  | 0
DE-5 | F110 | E-3 | 10 | 300 |  |  | 0
DE-6 | F108 | E-3 | 10 | 300 |  |  | 0
DE-7 | F107 | E-3 | 10 | 300 |  |  | 0
DE-8 | E128 | E-6 | 16 | 1200 |  |  | 0
DE-9 | E128 | E-6 | 16 | 1200 |  |  | 0
DE-10 | E118 | E-3 | 10 | 300 |  |  | 0
DE-11 | E115 | E-3 | 10 | 300 |  |  | 0
DE-12 | E113 | R-12 | 24X10 | 300 |  |  | 0
DE-13 | A132 | E-3 | 10 | 300 |  |  | 0
DE-14 | A130 | E-7 | 42X12 | 1600 |  |  | 0
DE-15 | C104 | E-1 | 6 | 100 |  |  | 0 | CHANGE CFM FROM 1000 TO 800, TYPE, SIZE
DE-16 | C122 | E-3 | 10 | 300 |  |  | 0
DE-17 | C105 | E-3 | 10 | 300 |  |  | 0
DE-18 | C106 | E-3 | 10 | 300 |  |  | 0
DE-19 | C117 | E-3 | 10 | 300 |  |  | 0
DE-20 | C108 | E-3 | 10 | 300 |  |  | 0
DE-21 | C116 | E-3 | 10 | 300 |  |  | 0
DE-22 | C109 | E-3 | 10 | 300 |  |  | 0
DE-23 | C114 | E-3 | 10 | 300 |  |  | 0
DE-24 | C111 | E-3 | 10 | 300 |  |  | 0
DE-25 | E106 | E-3 | 10 | 375 |  |  | 0
DE-26 | A128 | E-3 | 10 | 300 |  |  | 0
DE-27 | B101 | E-3 | 10 | 300 |  |  | 0
DE-28 | B104 | E-3 | 10 | 300 |  |  | 0
DE-29 | B105 | E-3 | 10 | 300 |  |  | 0
DE-30 | B118 | E-3 | 10 | 300 |  |  | 0
DE-31 | B107 | E-3 | 10 | 300 |  |  | 0
DE-32 | B116 | E-3 | 10 | 300 |  |  | 0
DE-33 | B108 | E-3 | 10 | 300 |  |  | 0
DE-34 | B115 | E-3 | 10 | 300 |  |  | 0
DE-35 | B112 | E-3 | 10 | 300 |  |  | 0
DE-36 | B113 | E-3 | 10 | 300 |  |  | 0
|  |  |  | 13775 |  | 0 | 0

## DOAS-1&2 EGRD's (2)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: DOAS-1&2 EGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
DE-37 | E133 | E-1 | 6 | 75 |  |  | 0
DE-38 | E134 | E-1 | 6 | 75 |  |  | 0
DE-39 | F102 | E-10 | 8X8 | 50 |  |  | 0 | CHANGED CFM FROM 75 TO 50, TYPE, SIZE
DE-40 | F100 | E-3 | 10 | 350 |  |  | 0 | CHANGED CFM FROM 150 TO 75
DE-41 | F101 | E-3 | 10 | 350 |  |  | 0 | CHANGED CFM FROM 150 TO 75
DE-42 | C128 | E-3 | 10 | 300 |  |  | 0
DE-43 | C127 | E-3 | 10 | 300 |  |  | 0
DE-44 | A112 | E-1 | 6 | 75 |  |  | 0
DE-45 | A104 | E-1 | 6 | 75 |  |  | 0
DE-46 | A107 | E-1 | 6 | 75 |  |  | 0
DE-47 | C124 | E-9 | 8X6 | 75 |  |  | 0
DE-48 | C125 | E-1 | 6 | 75 |  |  | 0
DE-49 | C126 | E-1 | 6 | 75 |  |  | 0
DE-50 | C224 | E-9 | 8X6 | 75 |  |  | 0
DE-51 | C225 | E-1 | 6 | 75 |  |  | 0
DE-52 | C226 | E-1 | 6 | 75 |  |  | 0
DE-53 | C228 | E-3 | 10 | 300 |  |  | 0
DE-54 | C227 | E-3 | 10 | 300 |  |  | 0
DE-55 | B127 | E-1 | 6 | 75 |  |  | 0
DE-56 | B126 | E-1 | 6 | 75 |  |  | 0
DE-57 | B125 | E-1 | 6 | 75 |  |  | 0
DE-58 | B128 | E-3 | 10 | 300 |  |  | 0
DE-59 | B129 | E-3 | 10 | 300 |  |  | 0
DE-60 | A123 | E-1 | 6 | 75 |  |  | 0
DE-61 | A117 | E-2 | 8 | 50 |  |  | 0
DE-62 | D126 | E-1 | 6 | 150 |  |  | 0 | CHANGED CFM FROM 150 TO 75, TYPE, SIZE
DE-63 | D108 | E-3 | 10 | 350 |  |  | 0
DE-64 | D107 | E-3 | 10 | 350 |  |  | 0
DE-65 | D105 | E-9 | 8X6 | 75 |  |  | 0
DE-66 | D104 | E-9 | 8X6 | 75 |  |  | 0
DE-67 | D119 | E-3 | 10 | 275 |  |  | 0
DE-68 | D118 | E-3 | 10 | 275 |  |  | 0
DE-69 | D121 | E-3 | 10 | 275 |  |  | 0
DE-70 | D120 | E-3 | 10 | 275 |  |  | 0
DE-71 | D135 | E-4 | 12 | 500 |  |  | 0
DE-72 | D136 | E-3 | 10 | 325 |  |  | 0
DE-73 | D137 | E-3 | 10 | 325 |  |  | 0
DE-74 | D128 | E-4 | 12 | 500 |  |  | 0
DE-75 | D102 | E-8 | 28X28 | 2600 |  |  | 0
|  |  |  | 10000 |  | 0 | 0

## DOAS-1&2 EGRD's (3)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: DOAS-1&2 EGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
DE-75 | C204 | E-2 | 8 | 160 |  |  | 0
DE-76 | C222 | E-3 | 10 | 300 |  |  | 0
DE-77 | C205 | E-3 | 10 | 300 |  |  | 0
DE-78 | C206 | E-3 | 10 | 300 |  |  | 0
DE-79 | C217 | E-3 | 10 | 300 |  |  | 0
DE-80 | C208 | E-3 | 10 | 300 |  |  | 0
DE-81 | C209 | E-3 | 10 | 300 |  |  | 0
DE-82 | C216 | E-3 | 10 | 300 |  |  | 0
DE-83 | C211 | E-3 | 10 | 300 |  |  | 0
DE-84 | C214 | E-3 | 10 | 300 |  |  | 0
|  |  |  | 2860 |  | 0 | 0

## OAV's (1)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: OAV's
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Ak (max)
OA1-1 | A125 | OAV-05 | 5 | 145 |  | 60
OA1-2 | A118 | OAV-05 | 5 | 60 |  | 60
OA1-5 | A100 | OAV-08 | 8 | 515 |  | 125
OA1-9 | A126 | OAV-08 | 8 | 375 |  | 125
OA1-10 | A129 | OAV-05 | 5 | 80 |  | 60
OA1-11 | A128 | OAV-08 | 8 | 375 |  | 125
OA1-12 | A130 | OAV-12 | 12 | 1225 |  | 300
OA1-13 | A132 | OAV-08 | 8 | 450 |  | 125
OB1-1A | B112 | OAV-08 | 8 | 430 |  | 125
OB1-1B | B108 | OAV-08 | 8 | 430 |  | 125
OB1-2A | B107 | OAV-08 | 8 | 400 |  | 125
OB1-2B | B105 | OAV-08 | 8 | 360 |  | 125
OB1-3A | B104 | OAV-08 | 8 | 360 |  | 125
OB1-3B | B101 | OAV-08 | 8 | 390 |  | 125
OB1-4A | B113 | OAV-08 | 8 | 400 |  | 125
OB1-4B | B115 | OAV-08 | 8 | 360 |  | 125
OB1-5A | B116 | OAV-08 | 8 | 350 |  | 125
OB1-5B | B118 | OAV-08 | 8 | 350 |  | 125
OB1-6A | B121 | OAV-05 | 5 | 190 |  | 60
OB1-6B | B124 | OAV-05 | 5 | 85 |  | 60
OC1-1 | C104 | OAV-05 | 5 | 180 |  | 60
OC1-2 | C105 | OAV-08 | 8 | 400 |  | 125
OC1-3A | C106 | OAV-08 | 8 | 360 |  | 125
OC1-3B | C108 | OAV-08 | 8 | 360 |  | 125
OC1-4A | C109 | OAV-08 | 8 | 360 |  | 125
OC1-4B | C111 | OAV-08 | 8 | 360 |  | 125
OC1-5 | HALL | OAV-05 | 5 | 175 |  | 60
OC1-6 | C123 | OAV-05 | 5 | 85 |  | 60
OC1-7A | C122 | OAV-08 | 8 | 430 |  | 125
OC1-7B | C117 | OAV-08 | 8 | 430 |  | 125
OC1-8A | C116 | OAV-08 | 8 | 360 |  | 125
OC1-8B | C114 | OAV-08 | 8 | 360 |  | 125
Note on C7: NTAB: BILLINGSLEY ONLY

## OAV's (2)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: OAV's
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Ak (max)
OD1-1 | D109 | OAV-10 | 10 | 875 |  | 210
OD1-2 | D110 | OAV-06 | 6 | 145 |  | 65
OD1-3 | D100 | OAV-08 | 8 | 650 |  | 125
OD1-4A | D102 | OAV-16 | 16 | 2950 |  | 575
OD1-4B | D102 | OAV-16 | 16 | 2950 |  | 575
OE1-1 | E105 | OAV-08 | 8 | 485 |  | 125
OE1-2 | E106 | OAV-08 | 8 | 475 |  | 125
OE1-3 | E103 | OAV-05 | 5 | 135 |  | 60
OE1-5 | E118 | OAV-08 | 8 | 375 |  | 125
OE1-6 | E113 | OAV-08 | 8 | 355 |  | 125
OE1-7 | E115 | OAV-08 | 8 | 355 |  | 125
OE1-8 | E122 | OAV-16 | 16 | 3440 |  | 575
OE1-9 | E127 | OAV-08 | 8 | 260 |  | 125
OF1-1 | F104 | OAV-08 | 8 | 385 |  | 125
OF1-2A | F105 | OAV-08 | 8 | 360 |  | 125
OF1-2B | F107 | OAV-08 | 8 | 360 |  | 125
OF1-3A | F113 | OAV-08 | 8 | 360 |  | 125
OF1-3B | F111 | OAV-08 | 8 | 360 |  | 125
OF1-4A | F110 | OAV-08 | 8 | 360 |  | 125
OF1-4B | F108 | OAV-08 | 8 | 360 |  | 125
OC2-1 | C205 | OAV-08 | 8 | 360 |  | 125
OC2-2 | C204 | OAV-05 | 5 | 185 |  | 60
OC2-3A | C206 | OAV-08 | 8 | 360 |  | 125
OC2-3B | C208 | OAV-08 | 8 | 360 |  | 125
OC2-4A | C209 | OAV-08 | 8 | 360 |  | 125
OC2-4B | C211 | OAV-08 | 8 | 360 |  | 125
OC2-5 | C219 | OAV-05 | 5 | 175 |  | 60
OC2-6 | C223 | OAV-06 | 6 | 65 |  | 65
OC2-7A | C222 | OAV-08 | 8 | 430 |  | 125
OC2-7B | C217 | OAV-08 | 8 | 430 |  | 125
OC2-8A | C216 | OAV-08 | 8 | 360 |  | 125
OC2-8B | C214 | OAV-08 | 8 | 360 |  | 125
OC2-9 | C215 | OAV-05 | 5 |  |  | 60
Note on C7: NTAB: BILLINGSLEY ONLY

## OAV SGRD's (1)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: OAV SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
OA11-1 | A125 | S-1 | 6 | 30 |  |  | 0
OA11-2 | HP A1-1 | DUCT |  | 30 |  |  | 0
OA11-3 | A114 | S-1 | 6 | 15 |  |  | 0
OA11-4 | HP A1-3 | DUCT |  | 70 |  |  | 0
OA1-1 |  |  |  | 145 |  | 0 | 0
OA12-1 | A118 | S-1 | 6 | 60 |  |  | 0
OA1-2 |  |  |  | 60 |  | 0 | 0
OA15-1 | A100 | S-12 | 16X8 | 250 |  |  | 0
OA15-2 | A001 | S-12 | 16X8 | 25 |  |  | 0
OA15-3 | HP A1-8 | DUCT |  | 80 |  |  | 0
OA15-4 | HP A1-6 | DUCT |  | 55 |  |  | 0
OA15-5 | HP A1-7 | DUCT |  | 105 |  |  | 0
OA1-5 |  |  |  | 515 |  | 0 | 0
OA19-1 | A126 | S-3 | 10 | 375 |  |  | 0
OA1-9 |  |  |  | 375 |  | 0 | 0
OA110-1 | A129 | S-1 | 6 | 50 |  |  | 0
OA110-2 | A129 | S-1 | 6 | 30 |  |  | 0
OA1-10 |  |  |  | 80 |  | 0 | 0
OA111-1 | A128 | S-3 | 10 | 375 |  |  | 0
OA1-11 |  |  |  | 375 |  | 0 | 0
OA112-1 | A130 | S-2 | 8 | 175 |  |  | 0
OA112-2 | A130 | S-2 | 8 | 175 |  |  | 0
OA112-3 | A130 | S-2 | 8 | 125 |  |  | 0
OA112-4 | A130 | S-2 | 8 | 175 |  |  | 0
OA112-5 | A130 | S-5 | 10X6 | 200 |  |  | 0
OA112-6 | A130 | S-2 | 8 | 175 |  |  | 0
OA112-7 | A130 | S-5 | 10X6 | 200 |  |  | 0
OA1-12 |  |  |  | 1225 |  | 0 | 0
OA113-1 | A132 | S-4 | 12 | 450 |  |  | 0
OA1-13 |  |  |  | 450 |  | 0 | 0

## OAV SGRD's (2)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: OAV SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
OB11A-1 | B112 | S-4 | 12 | 430 |  |  | 0
OB1-1A |  |  |  | 430 |  | 0 | 0
OB11B-1 | B108 | S-4 | 12 | 430 |  |  | 0
OB1-1B |  |  |  | 430 |  | 0 | 0
OB12A-1 | B107 | S-3 | 10 | 360 |  |  | 0 | CHANGE CFM FROM 400 TO 360
OB1-2A |  |  |  | 360 |  | 0 | 0
OB12B-1 | B105 | S-3 | 10 | 360 |  |  | 0
OB1-2B |  |  |  | 360 |  | 0 | 0
OB13A-1 | B104 | S-3 | 10 | 360 |  |  | 0
OB1-3A |  |  |  | 360 |  | 0 | 0
OB13B-1 | B101 | S-3 | 10 | 390 |  |  | 0
OB1-3B |  |  |  | 390 |  | 0 | 0
OB14A-1 | B113 | S-3 | 10 | 400 |  |  | 0
OB1-4A |  |  |  | 400 |  | 0 | 0
OB14B-1 | B115 | S-3 | 10 | 360 |  |  | 0
OB1-4B |  |  |  | 360 |  | 0 | 0
OB15A-1 | B116 | S-3 | 10 | 350 |  |  | 0
OB1-5A |  |  |  | 350 |  | 0 | 0
OB15B-1 | B118 | S-3 | 10 | 350 |  |  | 0
OB1-5B |  |  |  | 350 |  | 0 | 0
OB16A-1 | B121 | S-2 | 8 | 190 |  |  | 0
OB1-6A |  |  |  | 190 |  | 0 | 0
OB16B-1 | B124 | S-2 | 8 | 85 |  |  | 0
OB1-6B |  |  |  | 85 |  | 0 | 0
OC11-1 | C104 | S-2 | 8 | 180 |  |  | 0
OC1-1 |  |  |  | 180 |  | 0 | 0

## OAV SGRD's (3)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: OAV SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
OC12-1 | C105 | S-3 | 10 | 400 |  |  | 0
OC1-2 |  |  |  | 400 |  | 0 | 0
OC13A-1 | C106 | S-3 | 10 | 360 |  |  | 0
OC1-3A |  |  |  | 360 |  | 0 | 0
OC13B-1 | C108 | S-3 | 10 | 360 |  |  | 0
OC1-3B |  |  |  | 360 |  | 0 | 0
OC14A-1 | C109 | S-3 | 10 | 360 |  |  | 0
OC1-4A |  |  |  | 360 |  | 0 | 0
OC14B-1 | C111 | S-3 | 10 | 360 |  |  | 0
OC1-4B |  |  |  | 360 |  | 0 | 0
OC15-1 | HALL | S-1 | 6 | 25 |  |  | 0
OC15-2 | HALL | S-2 | 8 | 150 |  |  | 0
OC1-5 |  |  |  | 175 |  | 0 | 0
OC16-1 | C123 | S-1 | 6 | 85 |  |  | 0 | CHANGE CFM FROM 85 TO 75
OC1-6 |  |  |  | 85 |  | 0 | 0
OC17A-1 | C122 | S-4 | 12 | 430 |  |  | 0
OC1-7A |  |  |  | 430 |  | 0 | 0
OC17B-1 | C117 | S-4 | 12 | 430 |  |  | 0
OC1-7B |  |  |  | 430 |  | 0 | 0
OC17A-1 | C116 | S-3 | 10 | 360 |  |  | 0
OC1-8A |  |  |  | 360 |  | 0 | 0
OC18B-1 | C114 | S-3 | 10 | 360 |  |  | 0
OC1-8B |  |  |  | 360 |  | 0 | 0
OD11-1 | D109 | S-8 | 18X18 | 875 |  |  | 0
OD1-1 |  |  |  | 875 |  | 0 | 0

## OAV SGRD's (4)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: OAV SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
OD12-1 | D110 | S-2 | 8 | 100 |  |  | 0
OD12-2 | D131 | S-1 | 6 | 15 |  |  | 0
OD12-3 | D132 | S-1 | 6 | 15 |  |  | 0
OD12-4 | D133 | S-1 | 6 | 15 |  |  | 0
OD1-2 |  |  |  | 145 |  | 0 | 0
OD13-1 | D101 | S-3 | 10 | 250 |  |  | 0
OD13-2 | D100 | S-4 | 12 | 400 |  |  | 0
OD1-3 |  |  |  | 650 |  | 0 | 0
OD14A-1 | D102 | S-11 | 24X8 | 740 |  |  | 0
OD14A-2 | D102 | S-11 | 24X8 | 740 |  |  | 0 | CHANGE CFM FROM 735 TO 740
OD14A-3 | D102 | S-11 | 24X8 | 740 |  |  | 0 | CHANGE CFM FROM 735 TO 740
OD14A-4 | D102 | S-11 | 24X8 | 740 |  |  | 0
OD1-4A |  |  |  | 2960 |  | 0 | 0
OD14B-1 | D102 | S-11 | 24X8 | 740 |  |  | 0
OD14B-2 | D102 | S-11 | 24X8 | 740 |  |  | 0 | CHANGE CFM FROM 735 TO 740
OD14B-3 | D102 | S-11 | 24X8 | 740 |  |  | 0 | CHANGE CFM FROM 735 TO 740
OD14B-4 | D102 | S-11 | 24X8 | 740 |  |  | 0
OD1-4B |  |  |  | 2960 |  | 0 | 0
OE11-1 | E105 | S-4 | 12 | 485 |  |  | 0
OE1-1 |  |  |  | 485 |  | 0 | 0
OE12-1 | E106 | S-4 | 12 | 475 |  |  | 0
OE1-2 |  |  |  | 475 |  | 0 | 0
OE13-1 | HP E1-4 | DUCT |  | 75 |  |  | 0
OE13-2 | HP E1-3 | DUCT |  | 60 |  |  | 0
OE1-3 |  |  |  | 135 |  | 0 | 0
OE15-1 | E118 | S-3 | 10 | 375 |  |  | 0
OE1-5 |  |  |  | 375 |  | 0 | 0
OE16-1 | E118 | S-3 | 10 | 375 |  |  | 0
OE1-6 |  |  |  | 375 |  | 0 | 0
OE17-1 | E115 | S-3 | 10 | 355 |  |  | 0
OE1-7 |  |  |  | 355 |  | 0 | 0

## OAV SGRD's (5)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: OAV SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
OE18-1 | E121 | S-7 | 20X8 | 430 |  |  | 0
OE18-2 | E121 | S-7 | 20X8 | 430 |  |  | 0
OE18-3 | E121 | S-7 | 20X8 | 430 |  |  | 0
OE18-4 | E121 | S-7 | 20X8 | 430 |  |  | 0
OE18-5 | E121 | S-7 | 20X8 | 430 |  |  | 0
OE18-6 | E121 | S-7 | 20X8 | 430 |  |  | 0
OE18-7 | E121 | S-7 | 20X8 | 430 |  |  | 0
OE18-8 | E121 | S-7 | 20X8 | 430 |  |  | 0
OE1-8 |  |  |  | 3440 |  | 0 | 0
OE19-1 | E127 | S-3 | 10 | 260 |  |  | 0
OE1-9 |  |  |  | 260 |  | 0 | 0
OF11-1 | F104 | S-3 | 10 | 385 |  |  | 0
OF1-1 |  |  |  | 385 |  | 0 | 0
OF12A-1 | F105 | S-3 | 10 | 360 |  |  | 0
OF1-2A |  |  |  | 360 |  | 0 | 0
OF12B-1 | F107 | S-3 | 10 | 360 |  |  | 0
OF1-2B |  |  |  | 360 |  | 0 | 0
OF13A-1 | F113 | S-3 | 10 | 360 |  |  | 0
OF1-3A |  |  |  | 360 |  | 0 | 0
OF13B-1 | F111 | S-3 | 10 | 360 |  |  | 0
OF1-3B |  |  |  | 360 |  | 0 | 0
OF14A-1 | F110 | S-3 | 10 | 360 |  |  | 0
OF1-4A |  |  |  | 360 |  | 0 | 0
OF14B-1 | F108 | S-3 | 10 | 360 |  |  | 0
OF1-4B |  |  |  | 360 |  | 0 | 0
OC21-1 | C205 | S-3 | 10 | 360 |  |  | 0
OC2-1 |  |  |  | 360 |  | 0 | 0
OC22-1 | C204 | S-2 | 8 | 185 |  |  | 0
OC2-2 |  |  |  | 185 |  | 0 | 0

## OAV SGRD's (6)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: OAV SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
OC23A-1 | C206 | S-3 | 10 | 360 |  |  | 0
OC2-3A |  |  |  | 360 |  | 0 | 0
OC23B-1 | C208 | S-3 | 10 | 360 |  |  | 0
OC2-3B |  |  |  | 360 |  | 0 | 0
OC24A-1 | C209 | S-3 | 10 | 360 |  |  | 0
OC2-4A |  |  |  | 360 |  | 0 | 0
OC24B-1 | C211 | S-3 | 10 | 360 |  |  | 0
OC2-4B |  |  |  | 360 |  | 0 | 0
OC25-1 | C219 | S-1 | 6 | 25 |  |  | 0
OC25-2 | C232 | S-2 | 8 | 150 |  |  | 0
OC2-5 |  |  |  | 175 |  | 0 | 0
OC26-1 | C223 | S-1 | 6 | 65 |  |  | 0
OC2-6 |  |  |  | 65 |  | 0 | 0
OC27A-1 | C222 | S-4 | 12 | 430 |  |  | 0
OC2-7A |  |  |  | 430 |  | 0 | 0
OC27B-1 | C217 | S-4 | 12 | 430 |  |  | 0
OC2-7B |  |  |  | 430 |  | 0 | 0
OC28A-1 | C216 | S-3 | 10 | 250 |  |  | 0 | CHANGE CFM FROM 360 TO 250
OC2-8A |  |  |  | 250 |  | 0 | 0
OC28B-1 | C214 | S-3 | 10 | 360 |  |  | 0
OC2-8B |  |  |  | 360 |  | 0 | 0
OC29-1 | HP C2-9 | DUCT | 10 |  |  |  | #DIV/0!
OC2-9 |  |  |  | 0 |  | 0 | #DIV/0!

## EF B1-1
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: EF B1-1 |  |  | Area: B110 LAB EXHAUST
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-140-VG |  |  | CFM | 2200 |  | NEW EA CFM TOTAL
Serial Num |  |  |  |  | Fan RPM | 1225
Type |  | CRE DNBLAST |  |  | RL Voltage | 115
[5 empty] | RL Amperage | 8.8
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.335
Frame
Horsepower |  | 0.75
Motor Rpm |  | 1300
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 8.8
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EB11-1 | B108 | E-5 | 14 | 850 |  |  | 0
EB11-2 | B112 | E-5 | 14 | 850 |  |  | 0
EB11-3 | B110 | E-3 | 10 | 300 |  |  | 0 | CHANGE CFM FROM 275 TO 300
EB11-4 | B109 | E-2 | 8 | 200 |  |  | 0
EGRD's |  |  |  | 2200 |  | 0 | 0
NOTES: | EF DESIGN IS 2000 CFM, EGRD TOTAL IS 2175 CFM
-

## EF C1-1
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: EF C1-1 |  |  | Area: C120 LAB EXHAUST
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-140-VG |  |  | CFM | 2050 |  | NEW EA CFM TOTAL
Serial Num |  |  |  |  | Fan RPM | 1225
Type |  | CRE DNBLAST |  |  | RL Voltage | 115
[5 empty] | RL Amperage | 8.8
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.335
Frame
Horsepower |  | 0.75
Motor Rpm |  | 1300
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 8.8
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EB11-1 | C120 | E-2 | 8 | 175 |  |  | 0 | CHANGE CFM FROM 200 TO 175
EB11-2 | C121 | E-2 | 8 | 175 |  |  | 0
EB11-3 | C122 | E-4 | 12 | 850 |  |  | 0
EB11-4 | C117 | E-4 | 12 | 850 |  |  | 0
EGRD's |  |  |  | 2050 |  | 0 | 0
NOTES: | EF DESIGN IS 2000 CFM, EGRD TOTAL IS 2050 CFM
-

## EF C2-1
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: EF C2-1 |  |  | Area: C220 LAB EXHAUST
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-140-VG |  |  | CFM | 2050
Serial Num |  |  |  |  | Fan RPM | 1225
Type |  | CRE DNBLAST |  |  | RL Voltage | 115
[5 empty] | RL Amperage | 8.8
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.335
Frame
Horsepower |  | 0.75
Motor Rpm |  | 1300
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 8.8
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EC21-1 | C220 | E-2 | 8 | 200 |  |  | 0
EC21-2 | C221 | E-2 | 8 | 150 |  |  | 0
EC21-3 | C222 | E-4 | 12 | 850 |  |  | 0
EC21-4 | C217 | E-4 | 12 | 850 |  |  | 0
|  |  |  | 2050 |  | 0 | 0
-

## EF-2
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: EF-2 |  |  | Area: E101 KILN EXHAUST
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | CUE-090-VG |  |  | CFM | 500
Serial Num |  |  |  |  | Fan RPM | 1725
Type |  | CRE UPBLAST |  |  | RL Voltage | 115
[5 empty] | RL Amperage | 1.5
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.66
Frame
Horsepower |  | 0.1
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 1.5
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EF2-1 | E100 | DUCT |  | 500 |  |  | 0
|  |  |  | 500 |  | 0 | 0
-

## EF-3
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: EF-3 |  |  | Area: D101 CONCESSIONS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | CUE-090-VG |  |  | CFM | 600
Serial Num |  |  |  |  | Fan RPM | 1725
Type |  | CRE UPBLAST |  |  | RL Voltage | 115
[5 empty] | RL Amperage | 1.5
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.66
Frame
Horsepower |  | 0.1
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 1.5
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EF3-1 | D101 | E-4 |  | 600 |  |  | 0
#DIV/0!
#DIV/0!
#DIV/0!
|  |  |  | 600 |  | 0 | 0
NOTES: | EF DESIGN IS 495 CFM, EGRD TOTAL IS 600 CFM
-

## MAU (EF-4)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: EF-4 (MAU) |  | Area: KITCHEN MAKEUP AIR
Unit Data |  |  | Test Data
| Design | Actual |  | Design | Actual
MFG | GREENHECK |  | CFM | 3840
Model Num | SQ-160-VG |  | SF RPM | 1463
Serial Num |  |  | RL Voltage | 208
Type | CENT INLINE |  | RL Amperage | 6.5
Configuration |  |  | Suction ESP
Discharge ESP
|  |  | Total ESP | 0.5
Brake Horse Power
Motor Data
| Design | Actual
Motor MFG
Frame
Horsepower | 2
Motor Rpm | 1725
Phase | 3
Voltage (rated) | 208
Amperage (rated) | 6.5
Service Factor

## MAU (EF-4) GRD's
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: MAU (EF-4) SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
M-1 | KH-1 | DUCT | 8X24 | 960 |  |  | 0
M-2 | KH-1 | DUCT | 8X24 | 960 |  |  | 0
M-3 | KH-1 | DUCT | 8X24 | 960 |  |  | 0
M-4 | KH-2 | DUCT | 8X24 | 960 |  |  | 0
M-5 | KH-2 | DUCT | 8X24 | 960 |  |  | 0
M-6 | KH-2 | DUCT | 8X24 | 960 |  |  | 0
SGRD's |  |  |  | 5760 |  | 0 | 0
Asset: MAU (EF-4) EGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
RM-1 | E121 | T-2 | 48X24 | 2400 |  |  | 0
RM-2 | F113 | T-5 | 10 | 350 |  |  | 0
RM-3 | F111 | T-5 | 10 | 350 |  |  | 0
RM-4 | F110 | T-5 | 10 | 350 |  |  | 0
RM-5 | F108 | T-5 | 10 | 350 |  |  | 0
EGRD's |  |  |  | 3800 |  | 0 | 0

## EF B1-2
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: EF B1-2 |  | Area: B123 ELECTRICAL RM
Unit Data |  |  | Test Data
MFG | GREENHECK |  |  | Design | Actual
Model Num | CSP-A1050-VG |  | CFM | 600
Serial Num |  |  | Fan RPM | 772
Type | INLINE CABINET |  | RL Voltage | 115
|  |  | RL Amperage | 4.75
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.15
Frame
Horsepower | 56W
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated) | 4.75
Service Factor
-

## EF C1-2
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: EF C1-2 |  | Area: C130 ELECTRICAL RM
Unit Data |  |  | Test Data
MFG | GREENHECK |  |  | Design | Actual
Model Num | CSP-A1050-VG |  | CFM | 600
Serial Num |  |  | Fan RPM | 772
Type | INLINE CABINET |  | RL Voltage | 115
|  |  | RL Amperage | 4.75
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.15
Frame
Horsepower | 56W
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated) | 4.75
Service Factor
-

## EF C2-2
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: EF C2-2 |  | Area: C229 ELECTRICAL RM
Unit Data |  |  | Test Data
MFG | GREENHECK |  |  | Design | Actual
Model Num | CSP-A1050-VG |  | CFM | 600
Serial Num |  |  | Fan RPM | 772
Type | INLINE CABINET |  | RL Voltage | 115
|  |  | RL Amperage | 4.75
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.15
Frame
Horsepower | 56W
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated) | 4.75
Service Factor
-

## EF D1-1
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: EF D1-1 |  | Area: D115 ELECTRICAL RM
Unit Data |  |  | Test Data
MFG | GREENHECK |  |  | Design | Actual
Model Num | CSP-A1050-VG |  | CFM | 600
Serial Num |  |  | Fan RPM | 772
Type | INLINE CABINET |  | RL Voltage | 115
|  |  | RL Amperage | 4.75
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.15
Frame
Horsepower | 56W
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated) | 4.75
Service Factor
-

## EF-6
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: EF-6 |  | Area: E130 MAIN ELECT
Unit Data |  |  | Test Data
MFG | GREENHECK |  |  | Design | Actual
Model Num | SQ-160-VG |  | CFM | 1500
Serial Num |  |  | Fan RPM | 609
Type | CENT INLINE |  | RL Voltage | 115
|  |  | RL Amperage | 8.8
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.13
Frame
Horsepower | 0.75
Motor Rpm | 1140
Phase | 1
Voltage (rated) | 115
Amperage (rated) | 8.8
Service Factor
-

## EF-7
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: EF-7 |  | Area: E136 STORAGE
Unit Data |  |  | Test Data
MFG | GREENHECK |  |  | Design | Actual
Model Num | CSP-A190 |  | CFM | 150
Serial Num |  |  | Fan RPM | 1384
Type | INLINE CABINET |  | RL Voltage | 115
|  |  | RL Amperage | 0.45
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.38
Frame
Horsepower | 46W
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated) | 0.45
Service Factor
-

## EF-8
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: EF-8 |  | Area: CONCESSIONS BLDG
Unit Data |  |  | Test Data
MFG | GREENHECK |  |  | Design | Actual
Model Num | CUE-099-VG |  | CFM | 800
Serial Num |  |  | Fan RPM | 1565
Type | CRE UPBLST |  | RL Voltage | 115
|  |  | RL Amperage | 2.85
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.647
Frame
Horsepower | 0.25
Motor Rpm | 1725
Phase | 1
Voltage (rated) | 115
Amperage (rated) | 2.85
Service Factor
-

## KEF-1
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: KEF-1 |  | Area: KITCHEN HOODS KEH-1/2
Unit Data |  |  | Drive Data
MFG | GREENHECK |  | Motor Sheave Size
Model Num | CUBE-220HP-20 |  | Motor Bore Size
Serial Num |  |  | Fan Sheave Size
Type | CRE UPBLAST |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  | No of Belts
Motor MFG |  |  | Belt Size
Frame
Horsepower | 2 |  | Test Data
Motor Rpm | 1725 |  |  | Design | Actual
Phase | 3 |  | CFM | 4800
Voltage (rated) | 460 |  | Fan RPM | 1011
Amperage (rated) | 3.4 |  | RL Voltage | 460
Service Factor |  |  | RL Amperage | 3.4
Suction ESP
|  |  | Total ESP | 1
Brake Horse Power
-

## KEF-2
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: KEF-2 |  |  | Area: DISHWASHER
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | CUE-099-VG |  |  | CFM | 600
Serial Num |  |  |  |  | Fan RPM | 1363
Type |  | CRE UPBLAST |  |  | RL Voltage | 115
[5 empty] | RL Amperage | 2.85
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.603
Frame
Horsepower |  | 0.25
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 2.85
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EF2-1 | DW LOAD | PANTS LEG |  | 200 |  |  | 0
EF2-1 | DW UNLOAD | PANTS LEG |  | 400 |  |  | 0
|  |  |  | 600 |  | 0 | 0
-

## KH-1
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: KH-1 |  | Area: KITCHEN
Unit Data |  |  | Test Data Supply
MFG | GREENHECK |  |  | PRELIM | FINAL
Model Num | GHEW-144.00-S |  | AK factor
Job / Serial Num |  |  | Total AK Area | 15.1667
Type | TYPE I CANOPY |  | Kv factor (Vel) | 0.9
Hood length | 144 |  | Reading1 FPM
Hood Width | 66 |  | Reading2 FPM
Supply Plenum Type | EXTERNAL |  | Reading3 FPM
Supply Plenum Width | 14 |  | Reading4 FPM
Supply Plenum Length | 156 |  | Reading5 FPM
Reading6 FPM
Test Data Exhaust |  |  | Reading7 FPM
| PRELIM | FINAL | Reading8 FPM
Filter Type | BAFFLE |  | Reading9 FPM
Filter Size 1 | 20X16 |  | Reading10 FPM
Filter Qty 1 | 4 |  | Reading11 FPM
Filter AK factor size 1 | 2.25 |  | Reading12 FPM
Filter Total AK Area 1 | 9 |  | Reading13 FPM
Filter Size 2 | 20X20 |  | Reading14 FPM
Filter Qty 2 | 4 |  | Ave FPM(corr)
Filter AK factor size 2 | 2.4 |  | CFM | 2400
Filter Total AK Area 2 | 9.6
Filter1 FPM |  |  | Performance Data
Filter2 FPM |  |  |  | Design | Actual
Filter3 FPM |  |  | Exh-Supply Net CFM
Filter4 FPM |  |  | Smoke Generation Type
Filter5 FPM |  |  | Cooking Equip Heat On
Filter6 FPM |  |  | Hood Capture %
Filter7 FPM |  |  | Ambient Room Temp
Filter8 FPM |  |  | 100% override functional
Filter9 FPM
Filter Ave FPM |  |  | General
CFM | 1920 |  | Third Party Witness
Third Party Company
Cooking Equipment |  |  | Tech Witness
Item 1 |  |  | Tech Company
Item 2 |  |  | Code Official Witness
Item 3
Item 4
Item 5

## KH-2
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: KH-2 |  | Area: KITCHEN
Unit Data |  |  | Test Data Supply
MFG | GREENHECK |  |  | PRELIM | FINAL
Model Num | GHEW-144.00-S |  | AK factor
Job / Serial Num |  |  | Total AK Area | 15.1667
Type | TYPE I CANOPY |  | Kv factor (Vel) | 0.9
Hood length | 144 |  | Reading1 FPM
Hood Width | 66 |  | Reading2 FPM
Supply Plenum Type | EXTERNAL |  | Reading3 FPM
Supply Plenum Width | 14 |  | Reading4 FPM
Supply Plenum Length | 156 |  | Reading5 FPM
Reading6 FPM
Test Data Exhaust |  |  | Reading7 FPM
| PRELIM | FINAL | Reading8 FPM
Filter Type | BAFFLE |  | Reading9 FPM
Filter Size 1 | 20X16 |  | Reading10 FPM
Filter Qty 1 | 4 |  | Reading11 FPM
Filter AK factor size 1 | 2.25 |  | Reading12 FPM
Filter Total AK Area 1 | 9 |  | Reading13 FPM
Filter Size 2 | 20X20 |  | Reading14 FPM
Filter Qty 2 | 4 |  | Ave FPM(corr)
Filter AK factor size 2 | 2.4 |  | CFM | 2400
Filter Total AK Area 2 | 9.6
Filter1 FPM |  |  | Performance Data
Filter2 FPM |  |  |  | Design | Actual
Filter3 FPM |  |  | Exh-Supply Net CFM
Filter4 FPM |  |  | Smoke Generation Type
Filter5 FPM |  |  | Cooking Equip Heat On
Filter6 FPM |  |  | Hood Capture %
Filter7 FPM |  |  | Ambient Room Temp
Filter8 FPM |  |  | 100% override functional
Filter9 FPM
Filter Ave FPM |  |  | General
CFM | 1920 |  | Third Party Witness
Third Party Company
Cooking Equipment |  |  | Tech Witness
Item 1 |  |  | Tech Company
Item 2 |  |  | Code Official Witness
Item 3
Item 4
Item 5

## PUMP P-1A (1)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: P-1A |  | Service: GEOTHERMAL LOOP
Unit Data |  |  | Test Data
| Actual |  |  | Design | Actual
MFG | BELL & GOSSETT |  | Pump Off Pressure (psi)
Model Num | e-1510 2EB |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in)
Service | GEOTHERMAL LOOP |  | Valve Open GPM
Pump RPM | 1750 |  | Valve Open Diff (ft)
GPM/Head | 285 / 85 |  | Discharge Pressure (ft)
Impellar Diameter | 10.625 |  | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  |  | Final GPM
| Actual |  | Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame | 215T |  | RL Voltage | 460
Horsepower | 10 |  | RL Amperage
Motor RPM | 1800 |  | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## PUMP P-1A (2)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: P-1A |  | Service: GEOTHERMAL LOOP
Unit Data |  |  | Test Data
| Actual |  |  | Design | Actual
MFG | BELL & GOSSETT |  | Pump Off Pressure (psi)
Model Num | e-1510 2EB |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in)
Service | GEOTHERMAL LOOP |  | Valve Open GPM
Pump RPM | 1750 |  | Valve Open Diff (ft)
GPM/Head | 285 / 85 |  | Discharge Pressure (ft)
Impellar Diameter | 10.625 |  | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  |  | Final GPM
| Actual |  | Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame | 215T |  | RL Voltage | 460
Horsepower | 10 |  | RL Amperage
Motor RPM | 1800 |  | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## PUMP P-1B (1)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: P-1B |  | Service: GEOTHERMAL LOOP
Unit Data |  |  | Test Data
| Actual |  |  | Design | Actual
MFG | BELL & GOSSETT |  | Pump Off Pressure (psi)
Model Num | e-1510 2EB |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in)
Service | GEOTHERMAL LOOP |  | Valve Open GPM
Pump RPM | 1750 |  | Valve Open Diff (ft)
GPM/Head | 285 / 85 |  | Discharge Pressure (ft)
Impellar Diameter | 10.625 |  | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  |  | Final GPM
| Actual |  | Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame | 215T |  | RL Voltage | 460
Horsepower | 10 |  | RL Amperage
Motor RPM | 1800 |  | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## PUMP P-1B (2)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: P-1B |  | Service: GEOTHERMAL LOOP
Unit Data |  |  | Test Data
| Actual |  |  | Design | Actual
MFG | BELL & GOSSETT |  | Pump Off Pressure (psi)
Model Num | e-1510 2EB |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in)
Service | GEOTHERMAL LOOP |  | Valve Open GPM
Pump RPM | 1750 |  | Valve Open Diff (ft)
GPM/Head | 285 / 85 |  | Discharge Pressure (ft)
Impellar Diameter | 10.625 |  | Suction Pressure (ft)
Total Head Pressure (ft)
Motor Data |  |  | Final GPM
| Actual |  | Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame | 215T |  | RL Voltage | 460
Horsepower | 10 |  | RL Amperage
Motor RPM | 1800 |  | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## Circuit Setter (1)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: CIRCUIT SETTERS |  |  |  | Service:
Asset | Location | MFG | Model | Size | Type | Design GPM | Setting | Delta P | Final GPM | % to Design | HP TYPE | SIZE | GPM
D1-4A | D103 | IMI FLOW | AC-200 | 3 | Autoflow | 36 | 2-32 | 21.72 | 36 | 1 | 240 | 3 | 60
D1-1 | D111 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 12.07 | 12 | 1 | 48 | 1.25 | 12
D1-2 | D111 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 12.61 | 12 | 1 | 48 | 1.25 | 12
D1-3 | D111 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 11.58 | 12 | 1 | 48 | 1.25 | 12
D1-4B | D114 | IMI FLOW | AC-200 | 3 | Autoflow | 36 | 2-32 | 15.11 | 36 | 1 | 240 | 3 | 60
D1-5 | D114 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 13.67 | 12 | 1 | 48 | 1.25 | 12
E1-8A | E137 | IMI FLOW | AC-150 | 1.5 | Autoflow | 18 | 2-32 | 5.16 | 18 | 1 | 72 | 1.5 | 17
E1-8B | E137 | IMI FLOW | AC-150 | 1.5 | Autoflow | 18 | 2-32 | 6.15 | 18 | 1 | 72 | 1.5 | 17
A1-9 | E103 | IMI FLOW | AC-100 | 1 | Autoflow | 6 | 2-32 | 13.05 | 6 | 1 | 24 | 1 | 6
E1-1 | E103 | IMI FLOW | AC-125 | 1.25 | Autoflow | 9 | 2-32 | 14.71 | 9 | 1 | 36 | 1.25 | 9
A1-10 | E103 | IMI FLOW | AC-075 | 0.75 | Autoflow | 3 | 2-32 | 9.9 | 3 | 1 | 12 | 0.75 | 2.5
E1-2 | E103 | IMI FLOW | AC-100 | 1 | Autoflow | 6 | 2-32 | 19.99 | 6 | 1 | 24 | 1 | 6
A1-11 | E103 | IMI FLOW | AC-100 | 1 | Autoflow | 6 | 2-32 | 18.59 | 6 | 1 | 24 | 1 | 6
E1-4 | E103 | IMI FLOW | AC-075 | 0.75 | Autoflow | 3 | 2-32 | 16.48 | 3 | 1 | 12 | 0.75 | 2.5
E1-3 | E103 | IMI FLOW | AC-075 | 0.75 | Autoflow | 2 | 2-32 | 20.92 | 2 | 1 | 9 | 0.75 | 1.88
E1-5 | E103 | IMI FLOW | AC-100 | 1 | Autoflow | 6 | 2-32 | 20.14 | 6 | 1 | 24 | 1 | 6
A1-12 | E103 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 13.88 | 12 | 1 | 48 | 1.25 | 12
E1-6 | E103 | IMI FLOW | AC-100 | 1 | Autoflow | 6 | 2-32 | 20.41 | 6 | 1 | 24 | 1 | 6
A1-2 | B100 | IMI FLOW | AC-075 | 0.75 | Autoflow | 2 | 2-32 | 17.75 | 2 | 1 | 9 | 0.75 | 1.88
A1-4 | A124 | IMI FLOW | AC-075 | 0.75 | Autoflow | 1.5 | 2-32 | 10.48 | 1.5 | 1 | 6 | 0.75 | 1.25
A1-5 | A124 | IMI FLOW | AC-125 | 1.25 | Autoflow | 9 | 2-32 | 4.3 | 9 | 1 | 36 | 1.25 | 9
A1-1 | A124 | IMI FLOW | AC-075 | 0.75 | Autoflow | 1.5 | 2-32 | 10.15 | 1.5 | 1 | 6 | 0.75 | 1.25
A1-3 | A124 | IMI FLOW | AC-075 | 0.75 | Autoflow | 3 | 2-32 | 6.71 | 3 | 1 | 12 | 0.75 | 2.5
B1-3 | B103 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 5.61 | 12 | 1 | 48 | 1.25 | 12
B1-6 | B123A | IMI FLOW | AC-100 | 1 | Autoflow | 6 | 2-32 | 16 | 6 | 1 | 24 | 1 | 6
B1-7 | B123A | IMI FLOW | AC-075 | 0.75 | Autoflow | 3 | 2-32 | 7.06 | 3 | 1 | 12 | 0.75 | 2.5
B1-2 | B106 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 5.05 | 12 | 1 | 48 | 1.25 | 12
B1-5 | B117 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 4.19 | 12 | 1 | 48 | 1.25 | 12
B1-1 | B111 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 2.82 | 12 | 1 | 48 | 1.25 | 12
B1-4 | B114 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 3.77 | 12 | 1 | 48 | 1.25 | 12
E1-9 | E131 | IMI FLOW | AC-100 | 1 | Autoflow | 6 | 2-32 | 16.15 | 6 | 1 | 18 | 1 | 3.75
E1-10 | E131 | IMI FLOW | AC-150 | 1.5 | Autoflow | 15 | 2-32 | 4.02 | 15 | 1 | 60 | 1.5 | 15
E1-7 | E119 | IMI FLOW | AC-100 | 1 | Autoflow | 6 | 2-32 | 13.92 | 6 | 1 | 24 | 1 | 6
C1-5 | C130 | IMI FLOW | AC-075 | 0.75 | Autoflow | 3 | 2-32 | 10.11 | 3 | 1 | 9 | 0.75 | 1.88
A1-13 | C130 | IMI FLOW | AC-100 | 1 | Autoflow | 6 | 2-32 | 13.28 | 6 | 1 | 24 | 1 | 6
C1-6 | C130 | IMI FLOW | AC-075 | 0.75 | Autoflow | 2 | 2-32 | 12.71 | 2 | 1 | 12 | 0.75 | 2.5
A1-7 | A108 | IMI FLOW | AC-075 | 0.75 | Autoflow | 3 | 2-32 | 14.05 | 3 | 1 | 12 | 0.75 | 2.5
A1-8 | A108 | IMI FLOW | AC-075 | 0.75 | Autoflow | 2 | 2-32 | 11.33 | 2 | 1 | 9 | 0.75 | 1.88
A1-6 | A108 | IMI FLOW | AC-075 | 0.75 | Autoflow | 1.5 | 2-32 | 7.93 | 1.5 | 1 | 6 | 0.75 | 1.25

## Circuit Setter (2)
National TAB
Project: Selma Burke Middle School
Address: 235 Rinehardt Rd Mooresville, NC
Asset: CIRCUIT SETTERS |  |  |  | Service:
Asset | Location | MFG | Model | Size | Type | Design GPM | Setting | Delta P | Final GPM | % to Design | HP TYPE | SIZE | GPM
C1-1 | C103 | IMI FLOW | AC-075 | 0.75 | Autoflow | 3 | 2-32 | 6.2 | 3 | 1 | 12 | 0.75 | 2.5
C1-2 | C103 | IMI FLOW | AC-100 | 1 | Autoflow | 6 | 2-32 | 14.3 | 6 | 1 | 24 | 1 | 6
C1-3 | C107 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 5.85 | 12 | 1 | 48 | 1.25 | 12
C1-7 | C118 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 6.48 | 12 | 1 | 48 | 1.25 | 12
C1-8 | C115 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 2.59 | 12 | 1 | 48 | 1.25 | 12
C1-4 | C110 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 2.07 | 12 | 1 | 48 | 1.25 | 12
F1-1 | F103 | IMI FLOW | AC-125 | 1.25 | Autoflow | 9 | 2-32 | 5.86 | 9 | 1 | 36 | 1.25 | 9
F1-3 | F112 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 11.85 | 12 | 1 | 48 | 1.25 | 12
F1-2 | F106 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 10.46 | 12 | 1 | 48 | 1.25 | 12
F1-4 | F109 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 10.68 | 12 | 1 | 48 | 1.25 | 12
C2-5 | C231 | IMI FLOW | AC-075 | 0.75 | Autoflow | 3 | 2-32 | 6.19 | 3 | 1 | 12 | 0.75 | 2.5
C2-6 | C231 | IMI FLOW | AC-075 | 0.75 | Autoflow | 3 | 2-32 | 7.5 | 3 | 1 | 12 | 0.75 | 2.5
C2-2 | C203 | IMI FLOW | AC-100 | 1 | Autoflow | 6 | 2-32 | 5.85 | 6 | 1 | 18 | 1 | 3.75
C2-1 | C203 | IMI FLOW | AC-125 | 1.25 | Autoflow | 9 | 2-32 | 9.69 | 9 | 1 | 36 | 1.25 | 9
C2-7 | C218 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 3.94 | 12 | 1 | 48 | 1.25 | 12
C2-3 | C207 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 2.75 | 12 | 1 | 48 | 1.25 | 12
C2-9 | C215 | IMI FLOW | AC-100 | 1 | Autoflow | 6 | 2-32 | 6.91 | 6 | 1 | 18 | 1 | 3.75
C2-8 | C215 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 3.1 | 12 | 1 | 48 | 1.25 | 12
C2-4 | C210 | IMI FLOW | AC-125 | 1.25 | Autoflow | 12 | 2-32 | 2.11 | 12 | 1 | 48 | 1.25 | 12
NOTES: | E1-8A and 8B were closed to obtain enough at the end of C wing

## HP ZONE TABLE
[5 empty] | HP |  |  | OAV
| FLOOR | AREA | ROOM | M-301 | SIZE | ROOM POSITION | ZONE | TAG | SIZE | HP Model | HP DESIGN CFM
X | 1 | B | B111 | 2 | VHP-048 |  | B1-1 | OB1-1A / B | OAV-08 / OAV-08 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 1 | B | B106 | 2 | VHP-048 |  | B1-2 | OB1-2A / B | OAV-08 / OAV-08 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 1 | B | B103 | 2 | VHP-048 |  | B1-3 | OB1-3A / B | OAV-08 / OAV-08 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 1 | B | B114 | 2 | VHP-048 |  | B1-4 | OB1-4A / B | OAV-08 / OAV-08 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 1 | B | B117 | 2 | VHP-048 |  | B1-5 | OB1-5A / B | OAV-08 / OAV-08 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 1 | B | B123A | 6 | VHP-024 | RIGHT | B1-6 | OB1-6A / B | OAV-05 / OAV-05 | ClimateMaster TE-026 | HP DESIGN IS 800 CFM
X | 1 | B | B123A | 6 | VHP-012 | LEFT | B1-7 | OB1-7 | OAV-05 | ClimateMaster TS-012 | HP DESIGN IS 403 CFM
X | 1 | A | A124 | 4 | VHP-006 | LEFT CENTER | A1-1 | OA1-1 | OAV-05 | ClimateMaster TS-006 | HP DESIGN IS 168 CFM
X | 1 | A | B100 | 5 | VHP-009 |  | A1-2 | OA1-2 | OAV-05 | ClimateMaster TS-009 | HP DESIGN IS 230 CFM
X | 1 | A | A124 | 4 | VHP-012 | CENTER TOP | A1-3 | OA1-1 | SEE A1-1 | ClimateMaster TS-012 | HP DESIGN IS 403 CFM
X | 1 | A | A124 | 4 | VHP-006 | LEFT BOTTOM | A1-4 | OA1-1 | SEE A1-1 | ClimateMaster TS-006 | HP DESIGN IS 168 CFM
X | 1 | A | A124 | 4 | VHP-036 | RIGHT BOTTOM | A1-5 | OA1-5 | OAV-08 | ClimateMaster TE-038 | HP DESIGN IS 1200 CFM
X | 1 | A | A108 | 3 | VHP-006 | TOP | A1-6 | OA1-5 | SEE A1-5 | ClimateMaster TS-006 | HP DESIGN IS 168 CFM
X | 1 | A | A108 | 3 | VHP-012 | LEFT | A1-7 | OA1-5 | SEE A1-5 | ClimateMaster TS-012 | HP DESIGN IS 403 CFM
X | 1 | A | A108 | 3 | VHP-009 | RIGHT | A1-8 | OA1-5 | SEE A1-5 | ClimateMaster TS-009 | HP DESIGN IS 230 CFM
X | 1 | E | E103 | 12 | VHP-024 | TOP LEFT CORNER | A1-9 | OA1-9 | OAV-08 | ClimateMaster TE-026 | HP DESIGN IS 800 CFM
X | 1 | E | E103 | 12 | VHP-012 | TOP LEFT | A1-10 | OA1-10 | OAV-05 | ClimateMaster TS-012 | HP DESIGN IS 403 CFM
X | 1 | E | E103 | 12 | VHP-024 | TOP CENTER LEFT | A1-11 | OA1-11 | OAV-08 | ClimateMaster TE-026 | HP DESIGN IS 800 CFM
X | 1 | E | E103 | 12 | VHP-048 | TOP RIGHT | A1-12 | OA1-12 | OAV-12 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 1 | A | C130 | 8 | VHP-024 | LEFT BOTTOM | A1-13 | OA1-13 | OAV-08 | ClimateMaster TE-026 | HP DESIGN IS 800 CFM
X | 1 | C | C103 | 7 | VHP-012 | LEFT | C1-1 | OC1-1 | OAV-05 | ClimateMaster TS-012 | HP DESIGN IS 403 CFM
X | 1 | C | C103 | 7 | VHP-024 | RIGHT | C1-2 | OC1-2 | OAV-08 | ClimateMaster TE-026 | HP DESIGN IS 800 CFM
X | 1 | C | C107 | 2 | VHP-048 |  | C1-3 | OC1-3A / B | OAV-08 / OAV-08 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 1 | C | C110 | 2 | VHP-048 |  | C1-4 | OC1-4A / B | OAV-08 / OAV-08 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 1 | A | C130 | 8 | VHP-009 | LEFT TOP | C1-5 | OC1-5 | OAV-05 | ClimateMaster TS-009 | HP DESIGN IS 230 CFM
X | 1 | A | C130 | 8 | VHP-012 | RIGHT | C1-6 | OC1-6 | OAV-05 | ClimateMaster TS-012 | HP DESIGN IS 403 CFM
X | 1 | C | C118 | 2 | VHP-048 |  | C1-7 | OC1-7A / B | OAV-08 / OAV-08 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 1 | C | C115 | 2 | VHP-048 |  | C1-8 | OC1-8A / B | OAV-08 / OAV-08 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 1 | D | D111 | 11 | VHP-048 | LEFT TOP | D1-1 | OD1-1 | OAV-10 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 1 | D | D111 | 11 | VHP-048 | RIGHT TOP | D1-2 | OD1-2 | OAV-06 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 1 | D | D111 | 11 | VHP-048 | LEFT BOTTOM | D1-3 | OD1-3 | OAV-08 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 1 | D | D103 | 9 | VHP-240 |  | D1-4A | OD1-4A | OAV-16 | ClimateMaster TL-240 | HP DESIGN IS 8000 CFP
X | 1 | D | D114 | 10 | VHP-240 | RIGHT BOTTOM | D1-4B | OD1-4B | OAV-16 | ClimateMaster TL-240 | HP DESIGN IS 8000 CFP
X | 1 | D | D114 | 10 | VHP-048 | RIGHT TOP | D1-5 | OD1-2 | SEE D1-2 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 1 | E | E103 | 12 | VHP-036 | BOTTOM LEFT | E1-1 | OE1-1 | OAV-08 | ClimateMaster TE-038 | HP DESIGN IS 1200 CFM
X | 1 | E | E103 | 12 | VHP-024 | BOTTOM CENTER LEFT | E1-2 | OE1-2 | OAV-08 | ClimateMaster TE-026 | HP DESIGN IS 800 CFM
X | 1 | E | E103 | 12 | VHP-009 | TOP CENTER RIGHT | E1-3 | OE1-3 | OAV-05 | ClimateMaster TS-009 | HP DESIGN IS 230 CFM
X | 1 | E | E103 | 12 | VHP-012 | BOTTOM CENTER | E1-4 | OE1-3 | SEE E1-3 | ClimateMaster TS-012 | HP DESIGN IS 403 CFM
X | 1 | E | E103 | 12 | VHP-024 | BOTTOM CENTER RIGHT | E1-5 | OE1-5 | OAV-08 | ClimateMaster TE-026 | HP DESIGN IS 800 CFM
X | 1 | E | E103 | 12 | VHP-024 | BOTTOM RIGHT | E1-6 | OE1-6 | OAV-08 | ClimateMaster TE-026 | HP DESIGN IS 800 CFM
X | 1 | E | E119 | 13 | VHP-024 |  | E1-7 | OE1-7 | OAV-08 | ClimateMaster TE-026 | HP DESIGN IS 800 CFM
X | 1 | E | E137 | 14 | VHP-072 | LEFT TOP | E1-8A | OE1-8 | OAV-16 | ClimateMaster TE-072 | HP DESIGN IS 2300 CFM
X | 1 | E | E137 | 14 | VHP-072 | LEFT BOTTOM | E1-8B | OE1-8 | SEE E1-18A | ClimateMaster TE-072 | HP DESIGN IS 2300 CFM
X | 1 | E | E131 | 16 | VHP-018 | LEFT TOP | E1-9 | OE1-9 | OAV-06 | ClimateMaster TS-018 | HP DESIGN IS 573 CFM
X | 1 | E | E131 | 16 | VHP-060 | LEFT CENTER | E1-10 | NA | NA | ClimateMaster TE-064 | HP DESIGN IS 2000 CFM
X | 1 | F | F103 | 17 | VHP-036 |  | F1-1 | OF1-1 | OAV-08 | ClimateMaster TE-038 | HP DESIGN IS 1200 CFM
X | 1 | F | F106 | 2 | VHP-048 |  | F1-2 | OF1-2A / B | OAV-08 / OAV-08 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 1 | F | F112 | 2 | VHP-048 |  | F1-3 | OF1-3A / B | OAV-08 / OAV-08 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 1 | F | F109 | 2 | VHP-048 |  | F1-4 | OF1-2A / B | OAV-08 / OAV-08 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 2 | C | C203 |  | VHP-036 |  | C2-1 | OC2-1 | OAV-08 | ClimateMaster TE-038 | HP DESIGN IS 1200 CFM
X | 2 | C | C203 |  | VHP-018 |  | C2-2 | OC2-2 | OAV-05 | ClimateMaster TS-018 | HP DESIGN IS 573 CFM
X | 2 | C | C207 |  | VHP-048 |  | C2-3 | OC2-3A / B | OAV-08 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 2 | C | C210 |  | VHP-048 |  | C2-4 | OC2-4A / B | OAV-08 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 2 | C | C231 |  | VHP-012 | TOP | C2-5 | OC2-5 | OAV-05 | ClimateMaster TS-012 | HP DESIGN IS 403 CFM
X | 2 | C | C231 |  | VHP-012 | BOTTOM | C2-6 | OC2-6 | OAV-05 | ClimateMaster TS-012 | HP DESIGN IS 403 CFM
X | 2 | C | C218 |  | VHP-048 |  | C2-7 | OC2-7A / B | OAV-08 / OAV-08 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 2 | C | C215 |  | VHP-048 |  | C2-8 | OC2-8A / B | OAV-08 / OAV-08 | ClimateMaster TE-049 | HP DESIGN IS 1600 CFM
X | 2 | C | C215 |  | VHP-018 |  | C2-9 | OC2-9 | OAV-05 | ClimateMaster TS-018 | HP DESIGN IS 573 CFM