## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
FCU-1 | DINING | 2800 | 2769 | 2200 | 2136 | 600 | 633 | 21.43% | 22.86%
RTU-2 | KITCHEN | 3200 | 3144 | 0 | 0 | 3200 | 3144 | 100% | 100%
RTU-3 | BOH | 712 | 780 | 512 | 572 | 200 | 208 | 28.09% | 26.67%
KEF-1 | HD1 | [10 empty] | 2625 | 2608
KEF-2 | HD2 | [10 empty] | 975 | 916
EF-3 | RESTROOM | [12 empty] | 240 | 373
TOTALS |  | 6712 | 6693 | 2712 | 2708 | 4000 | 3985 |  |  | 0 | 0 | 3600 | 3524 | 240 | 373
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4000 | 3985 |  | FRONT |  | 0.0022 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3840 | 3897 |  | SIDE |  | 0.0001 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 160 | 88 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00115 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 3200 | 3144
TOTAL KITCHEN EXHAUST |  | 3600 | 3524
NET AIRFLOW |  | -400 | -380
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0