## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3000 | 2871 | 2500 | 2356 | 500 | 515 | 16.67% | 17.94%
RTU-2 | DINING | 3000 | 2983 | 2500 | 2452 | 500 | 531 | 16.67% | 17.8%
RTU-3 | KITCHEN | 2400 | 2229 | 2200 | 2025 | 200 | 204 | 8.333% | 9.152%
MUA-1 | COOKLINE | [8 empty] | 2821 | 2825
EF-1 | HD1 GRILL | [10 empty] | 1852 | 1808
EF-2 | HD2 FRYER | [10 empty] | 1662 | 1667
EF-3 | RESTROOM | [12 empty] | 200 | 186
TOTALS |  | 8400 | 8083 | 7200 | 6833 | 1200 | 1250 |  |  | 2821 | 2825 | 3514 | 3475 | 200 | 186
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4021 | 4075 |  | FRONT |  | 0.0012 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3714 | 3661 |  | SIDE |  | 0.0024 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 307 | 414 |  | REAR |  | 0.0019 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0018333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0