## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | FOOD SERVICE | 4500 | 4524 | 3800 | 3831 | 700 | 693 | 15.56% | 15.32%
RTU-2 | RETAIL | 3400 | 3412 | 3020 | 3016 | 380 | 396 | 11.18% | 11.61%
RTU-3 | FRONT OF HOUSE | 2400 | 2291 | 2200 | 2096 | 200 | 195 | 8.333% | 8.512%
EF-1 | RESTROOMS | [12 empty] | 375 | 372
EF-2 | FOOD SERVICE | [12 empty] | 400 | 393
EF-3 | TRASH/STAGING | [12 empty] | 200 | 209
TOTALS |  | 10300 | 10227 | 9020 | 8943 | 1280 | 1284 |  |  | 0 | 0 | 0 | 0 | 975 | 974
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1280 | 1284 |  | FRONT |  | 0.0056 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 975 | 974 |  | SIDE |  | 0.0032 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 305 | 310 |  | REAR |  | 0.0016 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0034667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0