## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | RETAIL | 3400 | 3383 | 2790 | 2777 | 610 | 606 | 17.94% | 17.91%
RTU-2 | FOOD SERVICE | 5000 | 4924 | 4100 | 4034 | 900 | 890 | 18% | 18.07%
RTU-3 | RETAIL | 3000 | 2985 | 2460 | 2455 | 540 | 530 | 18% | 17.76%
EF-1 | FOOD SERVICE | [12 empty] | 1550 | 2209
EF-2 | WATER SRVC RM | [12 empty] | 60 | 61
TOTALS |  | 11400 | 11292 | 9350 | 9266 | 2050 | 2026 |  |  | 0 | 0 | 0 | 0 | 1610 | 2270
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 2050 | 2026 |  | FRONT |  | -0.002 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 1610 | 2270 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 440 | -244 |  | REAR |  | -0.002 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.002 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Building pressure measurements are an estimate based on net airflow due to time constraints. Building pressure will be verified when EF-1 is rebalanced.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0