## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 5000 | 5080 | 4000 | 4124 | 1000 | 956 | 20% | 18.82%
DOAS-1 | KTICHEN | 2200 | 2355 | 0 | 0 | 2200 | 2355 | 100% | 100%
KEF-1 | HD 1 | [10 empty] | 1600 | 1344
KEF-2 | HD 2 | [10 empty] | 775 | 778
KEF-3 | HD 3 | [10 empty] | 525 | 558
EF-1 | RESTROOM | [12 empty] | 75 | 55
EF-2 | RESTROOM | [12 empty] | 75 | 73
TOTALS |  | 7200 | 7435 | 4000 | 4124 | 3200 | 3311 |  |  | 0 | 0 | 2900 | 2680 | 150 | 128
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3200 | 3311 |  | FRONT |  | -0.002 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3050 | 2808 |  | SIDE |  | 0.008 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 150 | 503 |  | REAR |  | -0.001 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0016667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0