## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 |  | 6000 | 8133 | 4800 | 6667 | 1200 | 1466 | 20% | 18.03%
RTU-2 |  | 6000 | 6506 | 4800 | 2615 | 1200 | 3891 | 20% | 59.81%
RTU-3 |  | 6000 | 4298 | 4800 | 4121 | 1200 | 177 | 20% | 4.118%
EF-1 | KITCHEN HD-1 | [10 empty] | 1330 | 1438
EF-2 | KITCHEN HD-2 | [10 empty] | 1350 | 1173
EF-3 | KITCHEN HD-3 | [10 empty] | 1327 | 1835
EF-4 | KITCHEN HD-4 | [10 empty] | 825 | 1268
EF-5 | KITCHEN HD | [10 empty] | 500 | 469
EF-6 | RESTROOM | [12 empty] | 525 | 363
TOTALS |  | 18000 | 18937 | 14400 | 13403 | 3600 | 5534 |  |  | 0 | 0 | 5332 | 6183 | 525 | 363
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3600 | 5534 |  | FRONT |  | -0.0514 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 5857 | 6546 |  | SIDE |  | -0.0468 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -2257 | -1012 |  | REAR |  | -0.0487 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.048967 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0