## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
OAU-1 | DINNING/KITCH. | 3300 | 3695 | 0 | -86 | 3300 | 3781 | 100% | 102.3%
EF-1 | HOOD 1 | [10 empty] | 1200 | 1161
EF-2 | HOOD 2 | [10 empty] | 1200 | 1208
EF-3 | RR | [12 empty] | 300 | 296
TOTALS |  | 3300 | 3695 | 0 | -86 | 3300 | 3781 |  |  | 0 | 0 | 2400 | 2369 | 300 | 296
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3300 | 3781 |  | FRONT |  | 0.008 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2700 | 2665 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 600 | 1116 |  | REAR |  | 0.017 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0125 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
RR EX FAN TIED TO LIGHT IN RR. REAR DOOR BUILD PRESSURE DID NOT CHANGE MUCH WHEN RR EX FAN TURNS ON BUT FRONT INTERANCE DID. WHEN RR FAN COMES ON FRONT DOOR BP DROPS FROM 0.008 TO 0.002 BUT IS STILL POSITIVE.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0