## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3000 | 3110 | 2070 | 2146 | 930 | 964 | 31% | 31%
RTU-2 | KITCHEN | 4000 | 4150 | 2400 | 2467 | 1600 | 1683 | 40% | 40.55%
FC-2 | FOH | 1880 | 1924 | 1495 | 1924 | 385 | 0 | 20.48% | 0%
EF-1 | KITCHEN HD 1 | [10 empty] | 860 | 877
EF-2 | KITCHEN HD 2 | [10 empty] | 738 | 730
EF-3 | KITCHEN HD 3 | [10 empty] | 738 | 721
EF-4 | RESTROOM | [12 empty] | 200 | 401
TOTALS |  | 8880 | 9184 | 5965 | 6537 | 2915 | 2647 |  |  | 0 | 0 | 2336 | 2328 | 200 | 401
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 2915 | 2647 |  | FRONT |  | -0.002 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 2536 | 2729 |  | SIDE |  | -0.005 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 379 | -82 |  | REAR |  | -0.0027 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0032333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 1600 | 1683
TOTAL KITCHEN EXHAUST |  | 2336 | 2328
NET AIRFLOW |  | -736 | -645
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0