## Report Sheet
STORE #: | 3565 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | SALEM, OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 2 END PANEL - 171" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 410258 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | JORDAN BEST | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | ZJ078N12R2B5EAA2A2 | N2K0207261 | RTU-1 | KITCHEN | 500 | 489 | 0 | 0 |  | 1727 | 1727 | 965 | 965 | 2 | 198.3 | 198.3 | 3 | 5.8 | 4.62 | 4.62 | 1.5315 | 1.5315 | 0%
YORK | ZJ120N24R2B5EAA2A2 | N2K0207272 | RTU-2 | DINING | 1000 | 1341 | 1000 | 1062 |  | 1668 | 1668 | 996 | 996 | 3 | 198.4 | 198.4 | 3 | 8.3 | 7.4 | 7.4 | 2.4542 | 2.4542 | 0%
CAPTIVE AIRE | A1-D.250-G10 | 4401784 | MUA-1 | HOOD 1 | 1950 | 1834 | 1700 | 1723 | No | 1764 | 1775 | 1045 | 982 | 2 | 197.6 | 197.1 | 3 | 5.38 | 2.78 | 2.66 | 0.91828 | 0.87642 | -4.559%
CAPTIVE AIRE | NCA24HPFA | 4401784 | EF-1 | HOOD 1 | 3200 | 1982 | 2450 | 1982 | No | 1760 | 1760 | 882 | 882 | 2 | 199.5 | 199.5 | 3 | 5.38 | 2.73 | 2.73 | 0.91043 | 0.91043 | 0%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3450 | 3664 | 2700 | 2785 |  | FRONT DOOR |  | 0.0086 |  |  | INITIAL | 5.8144 | 3664
|  |  | TOTAL EXHAUST |  | 3350 | 2132 | 2600 | 2132 |  | BACK DOOR |  | 0.0052 |  |  | FINAL | 5.7725 | 2785
|  |  | NET AIRFLOW |  | 100 | 1532 | 100 | 653 |  | AVERAGE |  | 0.0069 |  |  | ∆ | -0.041861 | -879
Issue List
Unit # | Description
Select from drop down list
MUA | MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
EF-1 | EF / Hood Filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
EF-1 | Suspected low flow due to dirty filters, removed one hood filter to weigh. It weighed 9.1 lbs, a clean filter is around 6.8 lbs.
Additional Notes:

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
EF / Not operational / The EF is not operational. Recommend servicing.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not operational / MUA is not operational. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / OA Filters / OA filters are not installed. Recommend installing
RTU / Thermostats / Gridpoint stats are in Fan Auto. Recommend programming for Fan on except if kitchen RTU is balanced for 0 CFM OA.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.