## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
WSHP-1 | KITCHEN | 3200 | 3401 | 2240 | 2352 | 960 | 1049 | 30% | 30.84%
WSHP-2 | DINING | 4000 | 3898 | 2800 | 2726 | 1200 | 1172 | 30% | 30.07%
EF-1 | COOK LINE | [10 empty] | 1900 | 1955
EF-2 | DISHHOOD | [12 empty] | 75 | 70
EF-3 | BATHROOM | [12 empty] | 150 | 153
TOTALS |  | 7200 | 7299 | 5040 | 5078 | 2160 | 2221 |  |  | 0 | 0 | 1900 | 1955 | 225 | 223
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2160 | 2221 |  | FRONT |  | 0.005 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2125 | 2178 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 35 | 43 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.005 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0