## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 2400 | 2401 | 1700 | 1586 | 700 | 815 | 29.17% | 33.94%
RTU-2 | KITCHEN | 5200 | 4973 | 4680 | 4463 | 520 | 510 | 10% | 10.26%
MUA-1 | COOKLINE | [8 empty] | 1976 | 1907
KEF-1 | KITCHEN HOOD | [10 empty] | 2381 | 2227
EF-1 | RESTROOM | [12 empty] | 100 | 193
EF-2 | RESTROOM | [12 empty] | 100 | 214
EF-3 | DISHWASH | [12 empty] | 100 | 108
TOTALS |  | 7600 | 7374 | 6380 | 6049 | 1220 | 1325 |  |  | 1976 | 1907 | 2381 | 2227 | 300 | 515
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3196 | 3232 |  | FRONT |  | 0.009 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2681 | 2742 |  | SIDE |  | NA |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 515 | 490 |  | REAR |  | 0.0046 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0068 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Increased OA for RTU-2 to account for EF's 1 and 2 being above design
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0