## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6150 | 6129 | 4450 | 4380 | 1700 | 1749 | 27.64% | 28.54%
RTU-2 | KITCHEN | 6225 | 6156 | 4550 | 4444 | 1675 | 1712 | 26.91% | 27.81%
PRV-2 | KITCHEN HD | [10 empty] | 1500 | 1490
PRV-3 | KITCHEN HD | [10 empty] | 1500 | 1510
PRV-1 | RESTROOM | [12 empty] | 300 | 310
EF-1 | MOP ROOM | [12 empty] | 75 | 0
TOTALS |  | 12375 | 12285 | 9000 | 8824 | 3375 | 3461 |  |  | 0 | 0 | 3000 | 3000 | 375 | 310
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3375 | 3461 |  | FRONT |  | 0.0076 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3375 | 3310 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | 151 |  | REAR |  | 0.0051 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00635 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0