## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8000 | 7563 | 5500 | 5171 | 2500 | 2392 | 31.25% | 31.63%
AC-2 | DINING B | 3050 | 2934 | 2370 | 2293 | 680 | 641 | 22.3% | 21.85%
AC-3 | DINING C | 3700 | 3736 | 2900 | 2908 | 800 | 828 | 21.62% | 22.16%
AC-4 | DINING A | 2750 | 2840 | 2150 | 2210 | 600 | 630 | 21.82% | 22.18%
AC-5 | PLAY GROUND | 1800 | 1820 | 1400 | 1402 | 400 | 418 | 22.22% | 22.97%
EF-1 | HOOD 1 LEFT | [10 empty] | 1085 | 1009
EF-2 | HOOD 1 RIGHT | [10 empty] | 1085 | 1186
EF-3 | RESTROOM | [12 empty] | 500 | 402
EF-4 | HOOD 2 | [10 empty] | 701 | 730
EF-5 | HOOD 3 | [10 empty] | 698 | 706
TOTALS |  | 19300 | 18893 | 14320 | 13984 | 4980 | 4909 |  |  | 0 | 0 | 3569 | 3631 | 500 | 402
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4980 | 4909 |  | FRONT |  | 0.0091 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 4069 | 4033 |  | SIDE |  | 0.013 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 911 | 876 |  | REAR |  | 0.0076 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0099 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390