## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | SALES | 2950 | 3100 | 2950 | 3100 | 0 | 0 | 0% | 0%
RTU-2 | SALES | 3400 | 3723 | 3400 | 3723 | 0 | 0 | 0% | 0%
RTU-3 | SALES | 3700 | 3783 | 3700 | 3783 | 0 | 0 | 0% | 0%
RTU-4 | SALES | 3600 | 3423 | 3600 | 3423 | 0 | 0 | 0% | 0%
RTU-5 | SALES | 3400 | 3420 | 3400 | 3420 | 0 | 0 | 0% | 0%
RTU-6 | SALES | 3000 | 3113 | 3000 | 3113 | 0 | 0 | 0% | 0%
RTU-7 | SALES | 3250 | 3216 | 3250 | 3216 | 0 | 0 | 0% | 0%
RTU-8 | SALES | 2950 | 3048 | 2271 | 3048 | 679 | 0 | 23.02% | 0%
RTU-9 | SALES | 3000 | 3063 | 3000 | 3063 | 0 | 0 | 0% | 0%
RTU-10 | PHARMACY | 2250 | 2278 | 1732 | 1734 | 518 | 544 | 23.02% | 23.88%
RTU-11 | DELI | 2000 | 2033 | 1880 | 1908 | 120 | 125 | 6% | 6.149%
RTU-12 | BAKERY | 1350 | 1328 | 1282 | 1328 | 68 | 0 | 5.037% | 0%
RTU-13 | BACKROOM | 1900 | 1990 | 1444 | 1556 | 456 | 434 | 24% | 21.81%
RTU-14 | BACKROOM | 2000 | 2099 | 1520 | 1629 | 480 | 470 | 24% | 22.39%
RTU-15 | DOCK | 2860 | 2991 | 2345 | 2508 | 515 | 483 | 18.01% | 16.15%
RTU-16 | BACK OFFICE | 2400 | 2352 | 1848 | 1756 | 552 | 596 | 23% | 25.34%
RTU-17 | PICKUP | 2400 | 2407 | 1920 | 1900 | 480 | 507 | 20% | 21.06%
RTU-18 | CART CORRAL | 2400 | 2441 | 2160 | 2185 | 240 | 256 | 10% | 10.49%
DOAS-1 | SALES | 4500 | 4510 | 0 | 0 | 4500 | 4510 | 100% | 100%
DOAS-2 | SALES | 4500 | 4439 | 0 | 0 | 4500 | 4439 | 100% | 100%
EF-4 | DELI HOOD | [10 empty] | 2400 | 2356
EF-9 | BAKERY OVEN | [12 empty] | 600 | 574
EF-10 | BAKERY OVEN | [12 empty] | 600 | 596
EF-1 | CUSTOMER RRS | [12 empty] | 750 | 752
EF-5 | FRONT ELECTRICAL | [12 empty] | 800 | 786
EF-6 | ELECTRICAL | [12 empty] | 800 | 838
EF-7 | SEAFOOD | [12 empty] | 700 | 723
EF-8 | CLEANING CENTER | [12 empty] | 200 | 201
EF-2 | FAMILY 2 | [12 empty] | 200 | 213
EF-3 | EMPLOYEE RRS | [12 empty] | 500 | 521
TOTALS |  | 57810 | 58757 | 44702 | 46393 | 13108 | 12364 |  |  | 0 | 0 | 2400 | 2356 | 5150 | 5204
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 13108 | 12364 |  | FRONT | [10 empty] | #DIV/0! | #DIV/0! | FALSE
TOTAL EXHAUST |  | 7550 | 7560 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 5558 | 4804 |  | REAR | [10 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
Open store. Unable to check building pressure due to customers frequently entering and exiting building.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0