## Report Sheet
STORE #: | 3514 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | BELLEFONTAINE, OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-03-18 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | JORDAN BEST | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | ZJ090N12D2B5HAA2A2 | N1G9123124 | RTU-1 | KITCHEN | 500 | 265 | 0 | 0 |  | 1737 | 1737 | 1016 | 1016 | 3 | 208.4 | 208.4 | 3 | 9.4 | 9.21 | 9.21 | 3.2085 | 3.2085 | 0%
YORK | ZJ120N18D2B5HAA2A1 | N1F9004634 | RTU-2 | DINING | 1000 | 270 | 1000 | 1050 |  | 1746 | 1746 | 953 | 953 | 3 | 209.8 | 209.8 | 3 | 9.4 | 8.53 | 8.53 | 2.9915 | 2.9915 | 0%
CAPTIVE AIRE | A1-D.250-G10 | 3964290 | MUA-1 | HOOD 1 | 1950 | 1971 | 1700 | 1795 | Yes | 1769 | 1782 | 1071 | 811 | 2 | 210 | 209 | 3 | 5.38 | 2.83 | 2.58 | 0.99345 | 0.90138 | -9.268%
CAPTIVE AIRE | NCA24HPFA | 3964290 | EF-1 | HOOD 1 | 3200 | 2799 | 2450 | 2215 | No | 1765 | 1768 | 863.5 | 845 | 2 | 209.8 | 209 | 3 | 5.38 | 3.77 | 3.5 | 1.3222 | 1.2228 | -7.516%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3450 | 2506 | 2700 | 2845 |  | FRONT DOOR |  | -0.057 |  |  | INITIAL | 8.5157 | 2506
|  |  | TOTAL EXHAUST |  | 3350 | 2949 | 2600 | 2365 |  | BACK DOOR |  | -0.054 |  |  | FINAL | 8.3242 | 2845
|  |  | NET AIRFLOW |  | 100 | -443 | 100 | 480 |  | AVERAGE |  | -0.0555 |  |  | ∆ | -0.19145 | 339
Issue List
Unit # | Description
Select from drop down list
MUA | MUA FAN RUNNING BACKWARDS INITIALLY
Additional Notes:

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
EF / Not operational / The EF is not operational. Recommend servicing.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not operational / MUA is not operational. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / OA Filters / OA filters are not installed. Recommend installing
RTU / Thermostats / Gridpoint stats are in Fan Auto. Recommend programming for Fan on except if kitchen RTU is balanced for 0 CFM OA.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.