Project Summary

The summary below provides a quick understanding of our scope of work and general testing procedures. Our focus is to work with the trades to remedy any issues or deficiencies during the actual field balancing and not after the balancing has occurred to achieve a positive environment and outcome. The level of success is determined by the availability of the trades, possible parts needed, or time constraints. This project consisted of the new construction of an automotive repair shop, Christian Brothers Automotive.  It included the balancing of one RTU serving the office area, two restroom exhaust fans, and two exhaust fans interlocked with louvres for relief. Enclosed in the report is further detail about these units and their performance.

RTU (Roof Top Units) w/ Diffusers

The RTU was measured at its terminal devices to establish a total flow for the unit. The RTU was adjusted to within tolerance of the engineer’s design flow. Each outlet was then adjusted to within tolerance of the design flow. Outside air was measured by reading the intake air opening with a velocity grid and multiplying by the free area. The outside air damper was adjusted until the airflow was within the design requirements. Any equipment that fell outside of that tolerance is noted throughout the report. The RTU is controlled by a wall thermostat and was programmed by the Mechanical Contractor.

Ceiling Exhaust Fans

The ceiling exhaust fans were measured using a flow hood. If speed adjustment was provided, the fan speed was adjusted to within design tolerance. Any equipment that fell outside of this tolerance is noted throughout the report. For EF-4, louvre operation as controlled by the wall thermostat was verified.

“Attic” Relief Fan

EF-3 was scheduled to be an inline attic fan. This was changed to an upblast fan installed on the roof. Fan operation is interlocked with a Louvre in the main shop area of the building for pressure relief. This operation was verified as controlled by a wall switch beneath the louvre. The fan was measured by reading the intake air grille with a velocity grid and multiplying by the free area. The motor sheave was adjusted until the airflow was within the design requirements.