## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AHU-1 |  | 33100 | 30685 | 33100 | 30685 | 0 | 0 | 0% | 0%
AC-1 | FRONT OFFICE | 1990 | 2102 | 1800 | 1822 | 190 | 280 | 9.548% | 13.32%
AC-2 | BAKERY | 2400 | 2534 | 2160 | 2300 | 240 | 234 | 10% | 9.234%
AC-3 | PHARMACY | 800 | 743 | 720 | 743 | 80 | 0 | 10% | 0%
AC-4 | LIQUOR | 4800 | 4565 | 4320 | 3591 | 480 | 974 | 10% | 21.34%
RTF-1 | FROZEN FOODS | [8 empty] | 5000 | 5249
HEF-1 | HOOD 1 | [10 empty] | 2500 | 2505
EF-3 | BAKERY RACK OVEN | [12 empty] | 800 | 486
EF-4 | RESTROOMS | [12 empty] | 330 | 396
EF-6 | ELECTRICAL ROOM | [12 empty] | 500 | 537
EF-7 | EMPLOYEE RESTROOMS | [12 empty] | 180 | 0
EF-9 | PHARMACY RESTROOM | [12 empty] | 70 | 0
TOTALS |  | 9990 | 9944 | 9000 | 8456 | 990 | 1488 |  |  | 5000 | 5249 | 2500 | 2505 | 1880 | 1419
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 5990 | 6737 |  | FRONT | [10 empty] | #DIV/0! | #DIV/0! | FALSE
TOTAL EXHAUST |  | 4380 | 3924 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 1610 | 2813 |  | REAR | [10 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0