## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 5000 | 3700 | 3750 | 3700 | 1250 | 0 | 25% | 0%
RTU-2 | KITCHEN | 5000 | 3060 | 4000 | 2275 | 1000 | 785 | 20% | 25.65%
EF-1 | HOOD1 | [10 empty] | 750 | 977
EF-2 | HOOD2 | [10 empty] | 800 | 716
EF-3 | RESTROOMS | [12 empty] | 300 | 0
TOTALS |  | 10000 | 6760 | 7750 | 5975 | 2250 | 785 |  |  | 0 | 0 | 1550 | 1693 | 300 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 2250 | 785 |  | FRONT |  | -0.006 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 1850 | 1693 |  | SIDE |  | -0.009 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 400 | -908 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0075 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0