## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KTICHEN | 4400 | 4354 | 3150 | 3053 | 1250 | 1301 | 28.41% | 29.88%
AC-2 | SIDE DINING | 3150 | 2877 | 2400 | 2186 | 750 | 691 | 23.81% | 24.02%
AC-3 | MAIN DINING | 4000 | 3845 | 3000 | 2817 | 1000 | 1028 | 25% | 26.74%
AC-4 | MAIN DINING | 2750 | 2845 | 2150 | 2243 | 600 | 602 | 21.82% | 21.16%
AC-5 | PLAY AREA | 2000 | 1830 | 1700 | 1517 | 300 | 313 | 15% | 17.1%
AC-6 | KTICHEN | 4400 | 4513 | 3450 | 3481 | 950 | 1032 | 21.59% | 22.87%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1957
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1091 | 1022
EF-3 | RESTROOM | [12 empty] | 500 | 451
TOTALS |  | 20700 | 20264 | 15850 | 15297 | 4850 | 4967 |  |  | 0 | 0 | 3003 | 2979 | 500 | 451
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4850 | 4967 |  | FRONT |  | 0.034 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3503 | 3430 |  | SIDE |  | 0.033 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1347 | 1537 |  | REAR |  | 0.032 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.033 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390