## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3850 | 3794 | 1390 | 1256 | 2460 | 2538 | 63.9% | 66.9%
RTU-2 | DINING | 2050 | 2009 | 500 | 412 | 1550 | 1597 | 75.61% | 79.49%
KEF-1 | GRILL HOOD | [10 empty] | 1994 | 1836
KEF-2 | FRYER HOOD | [10 empty] | 1216 | 1280
EF-1 | RESTROOMS | [12 empty] | 300 | 200
TOTALS |  | 5900 | 5803 | 1890 | 1668 | 4010 | 4135 |  |  | 0 | 0 | 3210 | 3116 | 300 | 200
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4010 | 4135 |  | FRONT |  | 0.0056 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3510 | 3316 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 500 | 819 |  | REAR |  | 0.0022 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0039
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0