## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RHP-1 | DINING | 5000 | 4044 | 4500 | 3553 | 500 | 491 | 10% | 12.14%
RHP-2 | KITCHEN | 4000 | 3947 | 3150 | 3105 | 850 | 842 | 21.25% | 21.33%
FC-1 | OFFICE |  |  |  |  | 20 | 21 | 100% | 100%
MUA-1 | COOKLINE | [8 empty] | 1950 | 1857
EF-1 | HOOD 1 | [10 empty] | 825 | 855
EF-2 | HOOD 2 | [10 empty] | 1811 | 1829
EF-3 | RESTROOMS | [12 empty] | 420 | 428
TOTALS |  | 9000 | 7991 | 7650 | 6658 | 1370 | 1354 |  |  | 1950 | 1857 | 2636 | 2684 | 420 | 428
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3320 | 3211 |  | FRONT |  | 0.0022 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3056 | 3112 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 264 | 99 |  | REAR |  | 0.0011 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00165 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2800 | 2699
TOTAL KITCHEN EXHAUST |  | 2636 | 2684
NET AIRFLOW |  | 164 | 15
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0