## ERV-H01
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: ERV-H01 |  | Area: HOTEL FLOORS 4-11
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | DAIKIN |  | Manufacturer | DAIKIN
Model Number | DPSA035 |  | Model Number | DPSA035
Serial Number |  |  | Serial Number
Configuration |  |  | Configuration
No. Pre Filters / Size |  |  | No. Pre Filters / Size
No. Pre Filters / Size |  |  | No. Pre Filters / Size
No. Pre Filters / Size |  |  | No. Pre Filters / Size
No. Final Filters / Size
No. Final Filters / Size
No. Final Filters / Size
Motor Data |  |  | Motor Data
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM |  |  | Horsepower / RPM
Rated Volts / Phase |  |  | Rated Volts / Phase
Rated Amperage / SF |  |  | Rated Amperage / SF
Drive Data |  |  | Drive Data
Motor Sheave Size / Bore |  |  | Motor Sheave Size / Bore
Fan Sheave Size / Bore |  |  | Fan Sheave Size / Bore
Belt CL Distance |  |  | Belt CL Distance
No. Belts / Size |  |  | No. Belts / Size
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 8160 |  | Total CFM | 6855
Fan RPM | 2282 |  | Fan RPM | 1351
VFD Speed |  |  | VFD Speed
RL Voltage |  |  | RL Voltage
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 7.48 |  | Motor B.H.P. | 3.61
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
System Set Point
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 3.83 |  | Total SP | 2.26
Final Filters P.D.
Heat Wheel P.D. |  |  | Heat Wheel P.D.
Pre Filters P.D. |  |  | Pre Filters P.D.
Total ESP | 2.50 |  | Total ESP | 1.50

## ERV-H01 SGRD (1)
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: ERV-H01 OUTSIDE AIR |  |  | Area: CORRIDORS & SERVICE LOBBIES
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | AREA
ERV1-1 | VRF-R09 | DUCT |  | 95 |  |  | 0 | 12A71
ERV1-2 | VRF-R08 | DUCT |  | 165 |  |  | 0 | 12A01
ERV1-3 | VRF-R01 | DUCT |  | 135 |  |  | 0 | 12A02
ERV1-4 | 11A01 | D1 | 12X6 | 220 |  |  | 0 | SA20
ERV1-5 | 10A01 | D1 | 12X6 | 220 |  |  | 0 | SA20
ERV1-6 | 9A01 | D1 | 12X6 | 220 |  |  | 0 | SA20
ERV1-7 | 8A01 | D1 | 12X6 | 220 |  |  | 0 | SA20
ERV1-8 | 7A01 | D1 | 12X6 | 220 |  |  | 0 | SA20
ERV1-9 | 6A01 | D1 | 12X6 | 220 |  |  | 0 | SA20
ERV1-10 | 5A01 | D1 | 12X6 | 220 |  |  | 0 | SA20
ERV1-11 | 4A01 | D1 | 12X6 | 220 |  |  | 0 | SA20
ERV1-12 | 11A01 | D1 | 12X6 | 220 |  |  | 0 | SA5
ERV1-13 | 10A01 | D1 | 12X6 | 220 |  |  | 0 | SA5
ERV1-14 | 9A01 | D1 | 12X6 | 220 |  |  | 0 | SA5
ERV1-15 | 8A01 | D1 | 12X6 | 220 |  |  | 0 | SA5
ERV1-16 | 7A01 | D1 | 12X6 | 220 |  |  | 0 | SA5
ERV1-17 | 6A01 | D1 | 12X6 | 220 |  |  | 0 | SA5
ERV1-18 | 5A01 | D1 | 12X6 | 220 |  |  | 0 | SA5
ERV1-19 | 4A01 | D1 | 12X6 | 220 |  |  | 0 | SA5
ERV1-20 | 11A04 | D5 | 8X6 | 100 |  |  | 0 | SA19
ERV1-21 | 10A04 | D5 | 8X6 | 100 |  |  | 0 | SA19
ERV1-22 | 9A04 | D5 | 8X6 | 100 |  |  | 0 | SA19
ERV1-23 | 8A04 | D5 | 8X6 | 100 |  |  | 0 | SA19
ERV1-24 | 7A04 | D5 | 8X6 | 100 |  |  | 0 | SA19
ERV1-25 | 6A04 | D5 | 8X6 | 100 |  |  | 0 | SA19
ERV1-26 | 5A04 | D5 | 8X6 | 100 |  |  | 0 | SA19
ERV1-27 | 4A04 | D5 | 8X6 | 100 |  |  | 0 | SA19
ERV1-28 | 11A01 | D1 | 12X6 | 220 |  |  | 0 | SA17
ERV1-29 | 10A01 | D1 | 12X6 | 220 |  |  | 0 | SA17
ERV1-30 | 9A01 | D1 | 12X6 | 220 |  |  | 0 | SA17
ERV1-31 | 8A01 | D1 | 12X6 | 220 |  |  | 0 | SA17
ERV1-32 | 7A01 | D1 | 12X6 | 220 |  |  | 0 | SA17
ERV1-33 | 6A01 | D1 | 12X6 | 220 |  |  | 0 | SA17
ERV-H01 PAGE 1 |  |  |  | 5940 |  | 0 | 0

## ERV-H01 SGRD (2)
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: ERV-H01 OUTSIDE AIR |  |  | Area: CORRIDORS & SERVICE LOBBIES
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | AREA
ERV1-34 | 5A01 | D1 | 12X6 | 220 |  |  | 0 | SA17
ERV1-35 | 4A01 | D1 | 12X6 | 220 |  |  | 0 | SA17
ERV1-36 | 11A01 | D1 | 12X6 | 220 |  |  | 0 | SA10
ERV1-37 | 10A01 | D1 | 12X6 | 220 |  |  | 0 | SA10
ERV1-38 | 9A01 | D1 | 12X6 | 220 |  |  | 0 | SA10
ERV1-39 | 8A01 | D1 | 12X6 | 220 |  |  | 0 | SA10
ERV1-40 | 7A01 | D1 | 12X6 | 220 |  |  | 0 | SA10
ERV1-41 | 6A01 | D1 | 12X6 | 220 |  |  | 0 | SA10
ERV1-42 | 5A01 | D1 | 12X6 | 220 |  |  | 0 | SA10
ERV1-43 | 4A01 | D1 | 12X6 | 220 |  |  | 0 | SA10
ERV-H01 PAGE 2 |  |  |  | 1760 |  | 0 | 0
ERV-H01 PAGE 1 |  |  |  | 5940 | 0 | 0 | 0
ERV-H01 TOTAL |  |  |  | 7700 |  | 0 | 0

## ERV-H01 EGRD (1)
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: ERV-H01 EXHAUST |  |  | Area: CORRIDORS & SERVICE LOBBIES
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design | AREA
EERV1-1 | 12A02C | G7 | 6X6 | 55 |  |  | 0 | FLR 12 | EVS CLOSET
EERV1-2 | 11A06 | J1 | 6X6 | 85 |  |  | 0 | EA19 | LOBBY
EERV1-3 | 11A04 | J1 | 6X6 | 115 |  |  | 0 | EA19 | CORRIDOR
EERV1-4 | 11A01 | J4 | 16X14 | 650 |  |  | 0 | EA19 | STORAGE
EERV1-5 | 10A06 | J1 | 6X6 | 85 |  |  | 0 | EA19 | LOBBY
EERV1-6 | 10A04 | J1 | 6X6 | 115 |  |  | 0 | EA19 | CORRIDOR
EERV1-7 | 10A01 | J4 | 16X14 | 650 |  |  | 0 | EA19 | STORAGE
EERV1-8 | 9A06 | J1 | 6X6 | 85 |  |  | 0 | EA19 | LOBBY
EERV1-9 | 9A04 | J1 | 6X6 | 115 |  |  | 0 | EA19 | CORRIDOR
EERV1-10 | 9A01 | J4 | 16X14 | 650 |  |  | 0 | EA19 | STORAGE
EERV1-11 | 8A06 | J1 | 6X6 | 85 |  |  | 0 | EA19 | LOBBY
EERV1-12 | 8A04 | J1 | 6X6 | 115 |  |  | 0 | EA19 | CORRIDOR
EERV1-13 | 8A01 | J4 | 16X14 | 650 |  |  | 0 | EA19 | STORAGE
EERV1-14 | 7A06 | J1 | 6X6 | 85 |  |  | 0 | EA19 | LOBBY
EERV1-15 | 7A04 | J1 | 6X6 | 115 |  |  | 0 | EA19 | CORRIDOR
EERV1-16 | 7A01 | J4 | 16X14 | 650 |  |  | 0 | EA19 | STORAGE
EERV1-17 | 6A06 | J1 | 6X6 | 85 |  |  | 0 | EA19 | LOBBY
EERV1-18 | 6A04 | J1 | 6X6 | 115 |  |  | 0 | EA19 | CORRIDOR
EERV1-19 | 6A01 | J4 | 16X14 | 650 |  |  | 0 | EA19 | STORAGE
EERV1-20 | 5A06 | J1 | 6X6 | 85 |  |  | 0 | EA19 | LOBBY
EERV1-21 | 5A04 | J1 | 6X6 | 115 |  |  | 0 | EA19 | CORRIDOR
EERV1-22 | 5A01 | J4 | 16X14 | 650 |  |  | 0 | EA19 | STORAGE
EERV1-23 | 4A06 | J1 | 6X6 | 85 |  |  | 0 | EA19 | LOBBY
EERV1-24 | 4A04 | J1 | 6X6 | 115 |  |  | 0 | EA19 | CORRIDOR
EERV1-25 | 4A01 | J4 | 16X14 | 650 |  |  | 0
ERV-H01 EA |  |  |  | 6855 |  | 0 | 0

## VRF-H47.1
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-H47.1 |  | Area: SERVICE LOBBY 4A04
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual | SUBMITTAL
Model Num | FXSQ12TBVJU |  |  |  | SA CFM | 370 |  | 335
Serial Num |  |  |  |  | Fan RPM
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
47.1-1 | 4A10 | D5 | 8X6 | 165 |  |  | 0
47.1-2 | 4A04 | D1 | 12X6 | 205 |  |  | 0
|  |  |  | 370 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-H52.1
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-H52.1 |  | Area: HSKPG STORAGE 4A06
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual | SUBMITTAL
Model Num | FXSQ12TBVJU |  |  |  | SA CFM | 375 |  | 335
Serial Num |  |  |  |  | Fan RPM
OA CFM
[5 empty] | RA CFM | 375
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
SUPPLY
52.1-1 | 4A02 | D4 | 16X6 | 375 |  |  | 0
|  |  |  | 375 |  | 0 | 0
RETURN | 4A01 | J2 | 16X8 | 375 |  |  | 0
R52.1-1 |  |  |  | 375 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-H47.2
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-H47.2 |  | Area: SERVICE LOBBY 5A04
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual | SUBMITTAL
Model Num | FXSQ12TBVJU |  |  |  | SA CFM | 370 |  | 335
Serial Num |  |  |  |  | Fan RPM
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
47.2-1 | 5A10 | D5 | 8X6 | 165 |  |  | 0
47.2-2 | 5A04 | D1 | 12X6 | 205 |  |  | 0
|  |  |  | 370 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-H52.2
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-H52.2 |  | Area: ELEV LOBBY 5A02
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual | SUBMITTAL
Model Num | FXSQ12TBVJU |  |  |  | SA CFM | 375 |  | 335
Serial Num |  |  |  |  | Fan RPM
OA CFM
[5 empty] | RA CFM | 375
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
SUPPLY
52.2-1 | 5A01 | E1 | 6 | 110 |  |  | 0
52.2-2 | 5A02 | D6 | 10X8 | 265 |  |  | 0
|  |  |  | 375 |  | 0 | 0
RETURN | 5A01 | J2 | 16X8 | 375 |  |  | 0
R52.3-1 |  |  |  | 375 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-H47.3
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-H47.3 |  | Area: SERVICE LOBBY 6A04
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual | SUBMITTAL
Model Num | FXSQ12TBVJU |  |  |  | SA CFM | 370 |  | 335
Serial Num |  |  |  |  | Fan RPM
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
47.3-1 | 6A10 | D5 | 8X6 | 165 |  |  | 0
47.3-2 | 6A04 | D1 | 12X6 | 205 |  |  | 0
|  |  |  | 370 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-H52.3
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-H52.3 |  | Area: ELEV LOBBY 6A02
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual | SUBMITTAL
Model Num | FXSQ12TBVJU |  |  |  | SA CFM | 375 |  | 335
Serial Num |  |  |  |  | Fan RPM
OA CFM
[5 empty] | RA CFM | 375
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
SUPPLY
52.3-1 | 6A01 | E1 | 6 | 110 |  |  | 0
52.3-2 | 6A02 | D6 | 10X8 | 265 |  |  | 0
|  |  |  | 375 |  | 0 | 0
RETURN | 6A01 | J2 | 16X8 | 375 |  |  | 0
R52.3-1 |  |  |  | 375 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-H47.4
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-H47.4 |  | Area: SERVICE LOBBY 7A04
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual | SUBMITTAL
Model Num | FXSQ12TBVJU |  |  |  | SA CFM | 370 |  | 335
Serial Num |  |  |  |  | Fan RPM
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
47.4-1 | 7A10 | D5 | 8X6 | 165 |  |  | 0
47.4-2 | 7A04 | D1 | 12X6 | 205 |  |  | 0
|  |  |  | 370 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-H52.4
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-H52.4 |  | Area: ELEV LOBBY 7A02
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual | SUBMITTAL
Model Num | FXSQ12TBVJU |  |  |  | SA CFM | 375 |  | 335
Serial Num |  |  |  |  | Fan RPM
OA CFM
[5 empty] | RA CFM | 375
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
SUPPLY
52.4-1 | 7A01 | E1 | 6 | 110 |  |  | 0
52.4-2 | 7A02 | D6 | 10X8 | 265 |  |  | 0
|  |  |  | 375 |  | 0 | 0
RETURN | 7A01 | J2 | 16X8 | 375 |  |  | 0
R52.4-1 |  |  |  | 375 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-H47.5
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-H47.5 |  | Area: SERVICE LOBBY 8A04
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual | SUBMITTAL
Model Num | FXSQ12TBVJU |  |  |  | SA CFM | 370 |  | 335
Serial Num |  |  |  |  | Fan RPM
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
47.5-1 | 8A10 | D5 | 8X6 | 165 |  |  | 0
47.5-2 | 8A04 | D1 | 12X6 | 205 |  |  | 0
|  |  |  | 370 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-H52.5
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-H52.5 |  | Area: ELEV LOBBY 8A02
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual | SUBMITTAL
Model Num | FXSQ12TBVJU |  |  |  | SA CFM | 375 |  | 335
Serial Num |  |  |  |  | Fan RPM
OA CFM
[5 empty] | RA CFM | 375
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
SUPPLY
52.5-1 | 8A01 | E1 | 6 | 110 |  |  | 0
52.5-2 | 8A02 | D6 | 10X8 | 265 |  |  | 0
|  |  |  | 375 |  | 0 | 0
RETURN | 8A01 | J2 | 16X8 | 375 |  |  | 0
R52.5-1 |  |  |  | 375 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-H47.6
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-H47.6 |  | Area: SERVICE LOBBY 9A04
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual | SUBMITTAL
Model Num | FXSQ12TBVJU |  |  |  | SA CFM | 370 |  | 335
Serial Num |  |  |  |  | Fan RPM
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
47.6-1 | 9A10 | D5 | 8X6 | 165 |  |  | 0
47.6-2 | 9A04 | D1 | 12X6 | 205 |  |  | 0
|  |  |  | 370 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-H52.6
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-H52.6 |  | Area: ELEV LOBBY 9A02
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual | SUBMITTAL
Model Num | FXSQ12TBVJU |  |  |  | SA CFM | 375 |  | 335
Serial Num |  |  |  |  | Fan RPM
OA CFM
[5 empty] | RA CFM | 375
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
SUPPLY
52.6-1 | 9A01 | E1 | 6 | 110 |  |  | 0
52.6-2 | 9A02 | D6 | 10X8 | 265 |  |  | 0
|  |  |  | 375 |  | 0 | 0
RETURN | 9A01 | J2 | 16X8 | 375 |  |  | 0
R56.5-1 |  |  |  | 375 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-H47.7
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-H47.7 |  | Area: SERVICE LOBBY 10A04
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual | SUBMITTAL
Model Num | FXSQ12TBVJU |  |  |  | SA CFM | 370 |  | 335
Serial Num |  |  |  |  | Fan RPM
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
47.7-1 | 10A10 | D5 | 8X6 | 165 |  |  | 0
47.7-2 | 10A04 | D1 | 12X6 | 205 |  |  | 0
|  |  |  | 370 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-H52.7
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-H52.7 |  | Area: ELEV LOBBY 10A02
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual | SUBMITTAL
Model Num | FXSQ12TBVJU |  |  |  | SA CFM | 375 |  | 335
Serial Num |  |  |  |  | Fan RPM
OA CFM
[5 empty] | RA CFM | 375
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
SUPPLY
52.7-1 | 10A01 | E1 | 6 | 110 |  |  | 0
52.7-2 | 10A02 | D6 | 10X8 | 265 |  |  | 0
|  |  |  | 375 |  | 0 | 0
RETURN | 10A01 | J2 | 16X8 | 375 |  |  | 0
R56.7-1 |  |  |  | 375 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-H47.8
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-H47.8 |  | Area: SERVICE LOBBY 11A04
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual | SUBMITTAL
Model Num | FXSQ12TBVJU |  |  |  | SA CFM | 370 |  | 335
Serial Num |  |  |  |  | Fan RPM
OA CFM
RA CFM
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
47.8-1 | 11A10 | D5 | 8X6 | 165 |  |  | 0
47.8-2 | 11A04 | D1 | 12X6 | 205 |  |  | 0
|  |  |  | 370 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-H52.8
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-H52.8 |  | Area: ELEV LOBBY 11A02
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual | SUBMITTAL
Model Num | FXSQ12TBVJU |  |  |  | SA CFM | 375 |  | 335
Serial Num |  |  |  |  | Fan RPM
OA CFM
[5 empty] | RA CFM | 375
Motor Data |  |  |  |  | RL Voltage
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase |  |  |  |  | Total ESP
Voltage (rated) |  |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
SUPPLY
52.8-1 | 11A01 | E1 | 6 | 110 |  |  | 0
52.8-2 | 11A02 | D6 | 10X8 | 265 |  |  | 0
|  |  |  | 375 |  | 0 | 0
RETURN | 11A01 | J2 | 16X8 | 375 |  |  | 0
R56.8-1 |  |  |  | 375 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## EF-H02
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H02 |  |  | Area: EA20 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-080-VG |  |  | CFM | 200
Serial Num |  |  |  |  | Fan RPM | 1684
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
H02-1 | H1198 RR | M1 | 4 | 25 |  |  | 0
H02-2 | H1098 RR | M1 | 4 | 25 |  |  | 0
H02-3 | H998 RR | M1 | 4 | 25 |  |  | 0
H02-4 | H898 RR | M1 | 4 | 25 |  |  | 0
H02-5 | H798 RR | M1 | 4 | 25 |  |  | 0
H02-6 | H698 RR | M1 | 4 | 25 |  |  | 0
H02-7 | H598 RR | M1 | 4 | 25 |  |  | 0
H02-8 | H498 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 200 |  | 0 | 0
-

## EF-H03
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H03 |  |  | Area: EA1 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH03-1 | H1196 RR | M1 | 4 | 25 |  |  | 0
EH03-2 | H1194 RR | M1 | 4 | 25 |  |  | 0
EH03-3 | H1096 RR | M1 | 4 | 25 |  |  | 0
EH03-4 | H1094 RR | M1 | 4 | 25 |  |  | 0
EH03-5 | H996 RR | M1 | 4 | 25 |  |  | 0
EH03-6 | H994 RR | M1 | 4 | 25 |  |  | 0
EH03-7 | H896 RR | M1 | 4 | 25 |  |  | 0
EH03-8 | H894 RR | M1 | 4 | 25 |  |  | 0
EH03-9 | H796 RR | M1 | 4 | 25 |  |  | 0
EH03-10 | H794 RR | M1 | 4 | 25 |  |  | 0
EH03-11 | H696 RR | M1 | 4 | 25 |  |  | 0
EH03-12 | H694 RR | M1 | 4 | 25 |  |  | 0
EH03-13 | H596 RR | M1 | 4 | 25 |  |  | 0
EH03-14 | H594 RR | M1 | 4 | 25 |  |  | 0
EH03-15 | H496 RR | M1 | 4 | 25 |  |  | 0
EH03-16 | H494 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## EF-H04
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H04 |  |  | Area: EA11 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH04-1 | H1187 RR | M1 | 4 | 25 |  |  | 0
EH04-2 | H1185RR | M1 | 4 | 25 |  |  | 0
EH04-3 | H1087 RR | M1 | 4 | 25 |  |  | 0
EH04-4 | H1085 RR | M1 | 4 | 25 |  |  | 0
EH04-5 | H987 RR | M1 | 4 | 25 |  |  | 0
EH04-6 | H985 RR | M1 | 4 | 25 |  |  | 0
EH04-7 | H887 RR | M1 | 4 | 25 |  |  | 0
EH04-8 | H885 RR | M1 | 4 | 25 |  |  | 0
EH04-9 | H787 RR | M1 | 4 | 25 |  |  | 0
EH04-10 | H785 RR | M1 | 4 | 25 |  |  | 0
EH04-11 | H687 RR | M1 | 4 | 25 |  |  | 0
EH04-12 | H685 RR | M1 | 4 | 25 |  |  | 0
EH04-13 | H587 RR | M1 | 4 | 25 |  |  | 0
EH04-14 | H585 RR | M1 | 4 | 25 |  |  | 0
EH04-15 | H487 RR | M1 | 4 | 25 |  |  | 0
EH04-16 | H485 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## EF-H05
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H05 |  |  | Area: EA2 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH05-1 | H1192 RR | M1 | 4 | 25 |  |  | 0
EH05-2 | H1190RR | M1 | 4 | 25 |  |  | 0
EH05-3 | H1092 RR | M1 | 4 | 25 |  |  | 0
EH05-4 | H1090 RR | M1 | 4 | 25 |  |  | 0
EH05-5 | H992 RR | M1 | 4 | 25 |  |  | 0
EH05-6 | H990 RR | M1 | 4 | 25 |  |  | 0
EH05-7 | H892 RR | M1 | 4 | 25 |  |  | 0
EH05-8 | H890 RR | M1 | 4 | 25 |  |  | 0
EH05-9 | H792 RR | M1 | 4 | 25 |  |  | 0
EH05-10 | H790 RR | M1 | 4 | 25 |  |  | 0
EH05-11 | H692 RR | M1 | 4 | 25 |  |  | 0
EH05-12 | H690 RR | M1 | 4 | 25 |  |  | 0
EH05-13 | H592 RR | M1 | 4 | 25 |  |  | 0
EH05-14 | H590 RR | M1 | 4 | 25 |  |  | 0
EH05-15 | H492 RR | M1 | 4 | 25 |  |  | 0
EH05-16 | H490 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## EF-H06
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H06 |  |  | Area: EA12 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH06-1 | H1183 RR | M1 | 4 | 25 |  |  | 0
EH06-2 | H1181RR | M1 | 4 | 25 |  |  | 0
EH06-3 | H1083 RR | M1 | 4 | 25 |  |  | 0
EH06-4 | H1081 RR | M1 | 4 | 25 |  |  | 0
EH06-5 | H983 RR | M1 | 4 | 25 |  |  | 0
EH06-6 | H981 RR | M1 | 4 | 25 |  |  | 0
EH06-7 | H883 RR | M1 | 4 | 25 |  |  | 0
EH06-8 | H881 RR | M1 | 4 | 25 |  |  | 0
EH06-9 | H783 RR | M1 | 4 | 25 |  |  | 0
EH06-10 | H781 RR | M1 | 4 | 25 |  |  | 0
EH06-11 | H683 RR | M1 | 4 | 25 |  |  | 0
EH06-12 | H681 RR | M1 | 4 | 25 |  |  | 0
EH06-13 | H583 RR | M1 | 4 | 25 |  |  | 0
EH06-14 | H581 RR | M1 | 4 | 25 |  |  | 0
EH06-15 | H483 RR | M1 | 4 | 25 |  |  | 0
EH06-16 | H481 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## EF-H07
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H07 |  |  | Area: EA13 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH07-1 | H1179 RR | M1 | 4 | 25 |  |  | 0
EH07-2 | H1177 RR | M1 | 4 | 25 |  |  | 0
EH07-3 | H1079 RR | M1 | 4 | 25 |  |  | 0
EH07-4 | H1077 RR | M1 | 4 | 25 |  |  | 0
EH07-5 | H979 RR | M1 | 4 | 25 |  |  | 0
EH07-6 | H977 RR | M1 | 4 | 25 |  |  | 0
EH07-7 | H879 RR | M1 | 4 | 25 |  |  | 0
EH07-8 | H877 RR | M1 | 4 | 25 |  |  | 0
EH07-9 | H779 RR | M1 | 4 | 25 |  |  | 0
EH07-10 | H777 RR | M1 | 4 | 25 |  |  | 0
EH07-11 | H679 RR | M1 | 4 | 25 |  |  | 0
EH07-12 | H677 RR | M1 | 4 | 25 |  |  | 0
EH07-13 | H579 RR | M1 | 4 | 25 |  |  | 0
EH07-14 | H577 RR | M1 | 4 | 25 |  |  | 0
EH07-15 | H479 RR | M1 | 4 | 25 |  |  | 0
EH07-16 | H477 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## EF-H08
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H08 |  |  | Area: EA3 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH08-1 | H1188 RR | M1 | 4 | 25 |  |  | 0
EH08-2 | H1186 RR | M1 | 4 | 25 |  |  | 0
EH08-3 | H1088 RR | M1 | 4 | 25 |  |  | 0
EH08-4 | H1086 RR | M1 | 4 | 25 |  |  | 0
EH08-5 | H988 RR | M1 | 4 | 25 |  |  | 0
EH08-6 | H986 RR | M1 | 4 | 25 |  |  | 0
EH08-7 | H888 RR | M1 | 4 | 25 |  |  | 0
EH08-8 | H886 RR | M1 | 4 | 25 |  |  | 0
EH08-9 | H788 RR | M1 | 4 | 25 |  |  | 0
EH08-10 | H786 RR | M1 | 4 | 25 |  |  | 0
EH08-11 | H688 RR | M1 | 4 | 25 |  |  | 0
EH08-12 | H686 RR | M1 | 4 | 25 |  |  | 0
EH08-13 | H588 RR | M1 | 4 | 25 |  |  | 0
EH08-14 | H586 RR | M1 | 4 | 25 |  |  | 0
EH08-15 | H488 RR | M1 | 4 | 25 |  |  | 0
EH08-16 | H486 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## EF-H09
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H09 |  |  | Area: EA4 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH09-1 | H1184 RR | M1 | 4 | 25 |  |  | 0
EH09-2 | H1182 RR | M1 | 4 | 25 |  |  | 0
EH09-3 | H1084 RR | M1 | 4 | 25 |  |  | 0
EH09-4 | H1082 RR | M1 | 4 | 25 |  |  | 0
EH09-5 | H984 RR | M1 | 4 | 25 |  |  | 0
EH09-6 | H982 RR | M1 | 4 | 25 |  |  | 0
EH09-7 | H884 RR | M1 | 4 | 25 |  |  | 0
EH09-8 | H882 RR | M1 | 4 | 25 |  |  | 0
EH09-9 | H784 RR | M1 | 4 | 25 |  |  | 0
EH09-10 | H782 RR | M1 | 4 | 25 |  |  | 0
EH09-11 | H684 RR | M1 | 4 | 25 |  |  | 0
EH09-12 | H682 RR | M1 | 4 | 25 |  |  | 0
EH09-13 | H584 RR | M1 | 4 | 25 |  |  | 0
EH09-14 | H582 RR | M1 | 4 | 25 |  |  | 0
EH09-15 | H484 RR | M1 | 4 | 25 |  |  | 0
EH09-16 | H482 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## EF-H10
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H10 |  |  | Area: EA14 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH10-1 | H1175 RR | M1 | 4 | 25 |  |  | 0
EH10-2 | H1173 RR | M1 | 4 | 25 |  |  | 0
EH10-3 | H1075 RR | M1 | 4 | 25 |  |  | 0
EH10-4 | H1073 RR | M1 | 4 | 25 |  |  | 0
EH10-5 | H975 RR | M1 | 4 | 25 |  |  | 0
EH10-6 | H973 RR | M1 | 4 | 25 |  |  | 0
EH10-7 | H875 RR | M1 | 4 | 25 |  |  | 0
EH10-8 | H873 RR | M1 | 4 | 25 |  |  | 0
EH10-9 | H775 RR | M1 | 4 | 25 |  |  | 0
EH10-10 | H773 RR | M1 | 4 | 25 |  |  | 0
EH10-11 | H675 RR | M1 | 4 | 25 |  |  | 0
EH10-12 | H673 RR | M1 | 4 | 25 |  |  | 0
EH10-13 | H575 RR | M1 | 4 | 25 |  |  | 0
EH10-14 | H573 RR | M1 | 4 | 25 |  |  | 0
EH10-15 | H475 RR | M1 | 4 | 25 |  |  | 0
EH10-16 | H473 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## EF-H11
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H11 |  |  | Area: EA5 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH11-1 | H1180 RR | M1 | 4 | 25 |  |  | 0
EH11-2 | H1178 RR | M1 | 4 | 25 |  |  | 0
EH11-3 | H1080 RR | M1 | 4 | 25 |  |  | 0
EH11-4 | H1078 RR | M1 | 4 | 25 |  |  | 0
EH11-5 | H980 RR | M1 | 4 | 25 |  |  | 0
EH11-6 | H978 RR | M1 | 4 | 25 |  |  | 0
EH11-7 | H880 RR | M1 | 4 | 25 |  |  | 0
EH11-8 | H878 RR | M1 | 4 | 25 |  |  | 0
EH11-9 | H780 RR | M1 | 4 | 25 |  |  | 0
EH11-10 | H778 RR | M1 | 4 | 25 |  |  | 0
EH11-11 | H680 RR | M1 | 4 | 25 |  |  | 0
EH11-12 | H678 RR | M1 | 4 | 25 |  |  | 0
EH11-13 | H580 RR | M1 | 4 | 25 |  |  | 0
EH11-14 | H578 RR | M1 | 4 | 25 |  |  | 0
EH11-15 | H480 RR | M1 | 4 | 25 |  |  | 0
EH11-16 | H478 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## EF-H12
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H12 |  |  | Area: EA15 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH12-1 | H1171 RR | M1 | 4 | 25 |  |  | 0
EH12-2 | H1169 RR | M1 | 4 | 25 |  |  | 0
EH12-3 | H1071 RR | M1 | 4 | 25 |  |  | 0
EH12-4 | H1069 RR | M1 | 4 | 25 |  |  | 0
EH12-5 | H971 RR | M1 | 4 | 25 |  |  | 0
EH12-6 | H969 RR | M1 | 4 | 25 |  |  | 0
EH12-7 | H871 RR | M1 | 4 | 25 |  |  | 0
EH12-8 | H869 RR | M1 | 4 | 25 |  |  | 0
EH12-9 | H771 RR | M1 | 4 | 25 |  |  | 0
EH12-10 | H769 RR | M1 | 4 | 25 |  |  | 0
EH12-11 | H671 RR | M1 | 4 | 25 |  |  | 0
EH12-12 | H669 RR | M1 | 4 | 25 |  |  | 0
EH12-13 | H571 RR | M1 | 4 | 25 |  |  | 0
EH12-14 | H569 RR | M1 | 4 | 25 |  |  | 0
EH12-15 | H471 RR | M1 | 4 | 25 |  |  | 0
EH12-16 | H469 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## EF-H13
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H13 |  |  | Area: EA6 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH13-1 | H1176 RR | M1 | 4 | 25 |  |  | 0
EH13-2 | H1174 RR | M1 | 4 | 25 |  |  | 0
EH13-3 | H1076 RR | M1 | 4 | 25 |  |  | 0
EH13-4 | H1074 RR | M1 | 4 | 25 |  |  | 0
EH13-5 | H976 RR | M1 | 4 | 25 |  |  | 0
EH13-6 | H974 RR | M1 | 4 | 25 |  |  | 0
EH13-7 | H876 RR | M1 | 4 | 25 |  |  | 0
EH13-8 | H874 RR | M1 | 4 | 25 |  |  | 0
EH13-9 | H776 RR | M1 | 4 | 25 |  |  | 0
EH13-10 | H774 RR | M1 | 4 | 25 |  |  | 0
EH13-11 | H676 RR | M1 | 4 | 25 |  |  | 0
EH13-12 | H674 RR | M1 | 4 | 25 |  |  | 0
EH13-13 | H576 RR | M1 | 4 | 25 |  |  | 0
EH13-14 | H574 RR | M1 | 4 | 25 |  |  | 0
EH13-15 | H476 RR | M1 | 4 | 25 |  |  | 0
EH13-16 | H474 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## EF-H14
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H14 |  |  | Area: EA16 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH14-1 | H1167 RR | M1 | 4 | 25 |  |  | 0
EH14-2 | H1165 RR | M1 | 4 | 25 |  |  | 0
EH14-3 | H1067 RR | M1 | 4 | 25 |  |  | 0
EH14-4 | H1065 RR | M1 | 4 | 25 |  |  | 0
EH14-5 | H967 RR | M1 | 4 | 25 |  |  | 0
EH14-6 | H965 RR | M1 | 4 | 25 |  |  | 0
EH14-7 | H867 RR | M1 | 4 | 25 |  |  | 0
EH14-8 | H865 RR | M1 | 4 | 25 |  |  | 0
EH14-9 | H767 RR | M1 | 4 | 25 |  |  | 0
EH14-10 | H765 RR | M1 | 4 | 25 |  |  | 0
EH14-11 | H667 RR | M1 | 4 | 25 |  |  | 0
EH14-12 | H665 RR | M1 | 4 | 25 |  |  | 0
EH14-13 | H567 RR | M1 | 4 | 25 |  |  | 0
EH14-14 | H565 RR | M1 | 4 | 25 |  |  | 0
EH14-15 | H467 RR | M1 | 4 | 25 |  |  | 0
EH14-16 | H465 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## EF-H15
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H15 |  |  | Area: EA7 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH15-1 | H1170 RR | M1 | 4 | 25 |  |  | 0
EH15-2 | H1172 RR | M1 | 4 | 25 |  |  | 0
EH15-3 | H1070 RR | M1 | 4 | 25 |  |  | 0
EH15-4 | H1072 RR | M1 | 4 | 25 |  |  | 0
EH15-5 | H970 RR | M1 | 4 | 25 |  |  | 0
EH15-6 | H972 RR | M1 | 4 | 25 |  |  | 0
EH15-7 | H870 RR | M1 | 4 | 25 |  |  | 0
EH15-8 | H872 RR | M1 | 4 | 25 |  |  | 0
EH15-9 | H770 RR | M1 | 4 | 25 |  |  | 0
EH15-10 | H772 RR | M1 | 4 | 25 |  |  | 0
EH15-11 | H670 RR | M1 | 4 | 25 |  |  | 0
EH15-12 | H672 RR | M1 | 4 | 25 |  |  | 0
EH15-13 | H570 RR | M1 | 4 | 25 |  |  | 0
EH15-14 | H572 RR | M1 | 4 | 25 |  |  | 0
EH15-15 | H470 RR | M1 | 4 | 25 |  |  | 0
EH15-16 | H472 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## EF-H16
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H16 |  |  | Area: EA8 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH16-1 | H1168 RR | M1 | 4 | 25 |  |  | 0
EH16-2 | H1166 RR | M1 | 4 | 25 |  |  | 0
EH16-3 | H1068 RR | M1 | 4 | 25 |  |  | 0
EH16-4 | H1066 RR | M1 | 4 | 25 |  |  | 0
EH16-5 | H968 RR | M1 | 4 | 25 |  |  | 0
EH16-6 | H966 RR | M1 | 4 | 25 |  |  | 0
EH16-7 | H868 RR | M1 | 4 | 25 |  |  | 0
EH16-8 | H866 RR | M1 | 4 | 25 |  |  | 0
EH16-9 | H768 RR | M1 | 4 | 25 |  |  | 0
EH16-10 | H766 RR | M1 | 4 | 25 |  |  | 0
EH16-11 | H668 RR | M1 | 4 | 25 |  |  | 0
EH16-12 | H666 RR | M1 | 4 | 25 |  |  | 0
EH16-13 | H568 RR | M1 | 4 | 25 |  |  | 0
EH16-14 | H566 RR | M1 | 4 | 25 |  |  | 0
EH16-15 | H468 RR | M1 | 4 | 25 |  |  | 0
EH16-16 | H466 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## EF-H17
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H17 |  |  | Area: EA9 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH17-1 | H1164 RR | M1 | 4 | 25 |  |  | 0
EH17-2 | H1162 RR | M1 | 4 | 25 |  |  | 0
EH17-3 | H1064 RR | M1 | 4 | 25 |  |  | 0
EH17-4 | H1062 RR | M1 | 4 | 25 |  |  | 0
EH17-5 | H964 RR | M1 | 4 | 25 |  |  | 0
EH17-6 | H962 RR | M1 | 4 | 25 |  |  | 0
EH17-7 | H864 RR | M1 | 4 | 25 |  |  | 0
EH17-8 | H862 RR | M1 | 4 | 25 |  |  | 0
EH17-9 | H764 RR | M1 | 4 | 25 |  |  | 0
EH17-10 | H762 RR | M1 | 4 | 25 |  |  | 0
EH17-11 | H664 RR | M1 | 4 | 25 |  |  | 0
EH17-12 | H662 RR | M1 | 4 | 25 |  |  | 0
EH17-13 | H564 RR | M1 | 4 | 25 |  |  | 0
EH17-14 | H562 RR | M1 | 4 | 25 |  |  | 0
EH17-15 | H464 RR | M1 | 4 | 25 |  |  | 0
EH17-16 | H462 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## EF-H18
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H18 |  |  | Area: EA10 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH18-1 | H1160 RR | M1 | 4 | 25 |  |  | 0
EH18-2 | H1158 RR | M1 | 4 | 25 |  |  | 0
EH18-3 | H1060 RR | M1 | 4 | 25 |  |  | 0
EH18-4 | H1058 RR | M1 | 4 | 25 |  |  | 0
EH18-5 | H960 RR | M1 | 4 | 25 |  |  | 0
EH18-6 | H958 RR | M1 | 4 | 25 |  |  | 0
EH18-7 | H860 RR | M1 | 4 | 25 |  |  | 0
EH18-8 | H858 RR | M1 | 4 | 25 |  |  | 0
EH18-9 | H760 RR | M1 | 4 | 25 |  |  | 0
EH18-10 | H758 RR | M1 | 4 | 25 |  |  | 0
EH18-11 | H660 RR | M1 | 4 | 25 |  |  | 0
EH18-12 | H658 RR | M1 | 4 | 25 |  |  | 0
EH18-13 | H560 RR | M1 | 4 | 25 |  |  | 0
EH18-14 | H558 RR | M1 | 4 | 25 |  |  | 0
EH18-15 | H460 RR | M1 | 4 | 25 |  |  | 0
EH18-16 | H458 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## EF-H19
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H19 |  |  | Area: EA17 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH19-1 | H1163 RR | M1 | 4 | 25 |  |  | 0
EH19-2 | H1161 RR | M1 | 4 | 25 |  |  | 0
EH19-3 | H1063 RR | M1 | 4 | 25 |  |  | 0
EH19-4 | H1061 RR | M1 | 4 | 25 |  |  | 0
EH19-5 | H963 RR | M1 | 4 | 25 |  |  | 0
EH19-6 | H961 RR | M1 | 4 | 25 |  |  | 0
EH19-7 | H863 RR | M1 | 4 | 25 |  |  | 0
EH19-8 | H861 RR | M1 | 4 | 25 |  |  | 0
EH19-9 | H763 RR | M1 | 4 | 25 |  |  | 0
EH19-10 | H761 RR | M1 | 4 | 25 |  |  | 0
EH19-11 | H663 RR | M1 | 4 | 25 |  |  | 0
EH19-12 | H661 RR | M1 | 4 | 25 |  |  | 0
EH19-13 | H563 RR | M1 | 4 | 25 |  |  | 0
EH19-14 | H561 RR | M1 | 4 | 25 |  |  | 0
EH19-15 | H464 RR | M1 | 4 | 25 |  |  | 0
EH19-16 | H461 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## EF-H20
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-H20 |  |  | Area: EA18 HOTEL ROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 400
Serial Num |  |  |  |  | Fan RPM | 1636
Type |  | CRE DNBLAST |  |  | RL Voltage
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.65
Frame
Horsepower
Motor Rpm
Phase
Voltage (rated)
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EH20-1 | H1159 RR | M1 | 4 | 25 |  |  | 0
EH20-2 | H1157 RR | M1 | 4 | 25 |  |  | 0
EH20-3 | H1059 RR | M1 | 4 | 25 |  |  | 0
EH20-4 | H1057 RR | M1 | 4 | 25 |  |  | 0
EH20-5 | H959 RR | M1 | 4 | 25 |  |  | 0
EH20-6 | H957 RR | M1 | 4 | 25 |  |  | 0
EH20-7 | H859 RR | M1 | 4 | 25 |  |  | 0
EH20-8 | H857 RR | M1 | 4 | 25 |  |  | 0
EH20-9 | H759 RR | M1 | 4 | 25 |  |  | 0
EH20-10 | H757 RR | M1 | 4 | 25 |  |  | 0
EH20-11 | H659 RR | M1 | 4 | 25 |  |  | 0
EH20-12 | H657 RR | M1 | 4 | 25 |  |  | 0
EH20-13 | H559 RR | M1 | 4 | 25 |  |  | 0
EH20-14 | H557 RR | M1 | 4 | 25 |  |  | 0
EH20-15 | H459 RR | M1 | 4 | 25 |  |  | 0
EH20-16 | H457 RR | M1 | 4 | 25 |  |  | 0
|  |  |  | 400 |  | 0 | 0
-

## PPF-H03
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: PPF-H03 |  |  | Area: HOTEL PURGE (POST FIRE SMOKE)
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-33 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | UNIV SNGL WIDTH |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  |  |  |  | Test Data
Motor Rpm | [5 empty] | Design | Actual
Phase |  |  |  |  | CFM | 14000
Voltage (rated) |  |  |  |  | Fan RPM | 831
Amperage (rated) |  |  |  |  | RL Voltage
Service Factor |  |  |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1.8
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
PF3-1 | FLR 12 RR HALL | J5 | 44X44 |  |  |  | #DIV/0!
PF3-2 | H1157 RR | J5 | 44X44 |  |  |  | #DIV/0!
PF3-3 | H1059 RR | J5 | 44X44 |  |  |  | #DIV/0!
PF3-4 | H1057 RR | J5 | 44X44 |  |  |  | #DIV/0!
PF3-5 | H959 RR | J5 | 44X44 |  |  |  | #DIV/0!
PF3-6 | H957 RR | J5 | 44X44 |  |  |  | #DIV/0!
PF3-7 | H859 RR | J5 | 44X44 |  |  |  | #DIV/0!
PF3-8 | H857 RR | J5 | 44X44 |  |  |  | #DIV/0!
PF3-9 | 4A01 | J5 | 44X44 |  |  |  | #DIV/0!
-

## SPF-H01
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: SPF-H01 |  |  | Area: SP1 (STAIR 01)
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-27 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | UNIV SINGLE WIDTH |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  |  |  |  | Test Data
Motor Rpm | [5 empty] | Design | Actual
Phase |  |  |  |  | CFM | 7600 |  | RATED 11,400 CFM
Voltage (rated) |  |  |  |  | Fan RPM
Amperage (rated) |  |  |  |  | RL Voltage
Service Factor |  |  |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
SPH01-1 | S1 ROOF-1 | D9 | 26X22 | 1900 |  |  | 0
SPH01-2 | S1 FLR 12 | D9 | 26X22 | 1900 |  |  | 0
SPH01-3 | S1 FLR 11 | D9 | 26X22 | 1900 |  |  | 0
SPH01-4 | S1 FLR 10 | D9 | 26X22 | 1900 |  |  | 0
|  |  |  | 7600 | 0 | 0 | 0
-

## SPF-H02
National TAB
Project: Harrah's River Valley Hotel (Murphy, NC)
Address: 777 Casino Parkway Murphy, NC 28906
Asset: SPF-H02 |  |  | Area: SP2 (STAIR 02)
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-18 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | UNIV SINGLE WIDTH |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  |  |  |  | Test Data
Motor Rpm | [5 empty] | Design | Actual
Phase |  |  |  |  | CFM | 2550 |  | RATED 3060 CFM
Voltage (rated) |  |  |  |  | Fan RPM | 1138
Amperage (rated) |  |  |  |  | RL Voltage
Service Factor |  |  |  |  | RL Amperage
Suction ESP
[5 empty] | Total ESP | 1
Brake Horse Power
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
SPH02-1 | S2 FLR 11 | D7 | 18X18 | 850 |  |  | 0
SPH02-2 | S2 FLR 10 | D7 | 18X18 | 850 |  |  | 0
SPH02-3 | S2 FLR 9 | D7 | 18X18 | 850 |  |  | 0
|  |  |  | 2550 |  | 0 | 0
-