## RTU-C01
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C01 |  | Area:
Supply Side
Unit Data |  |  | Test Data |  |  | USE FOR:
Manufacturer | DAIKIN |  |  | Design | Actual | VAV's
Model Number | MPS030FG4DV1CB |  | Supply CFM | 6500 |  | No Return Fan
Serial Number | FBOU203400668 |  | Min OA CFM | 1440
Configuration | VERTICAL |  | Return CFM | 5060
No. Pre Filters / Size | 8 / 24X24X2 |  | Fan RPM | 1506 |  | Remove unused fields:
No. Pre Filters / Size |  |  | Operating HZ |  |  | Heat Wheel
No. Pre Filters / Size |  |  | RL Voltage | 460 |  | CW/HW Coil (Change to DX coil if applicable)
No. Final Filters / Size |  |  | RL Amperage | 9.7
No. Final Filters / Size |  |  | Motor B.H.P. | 6.20
No. Final Filters / Size
Performance Data
Motor Data X |  |  |  | Design | Actual
Motor MFG / Frame | DAIKEN |  | Suction S.P.
Horsepower / RPM | 7.5 / 1770 |  | Discharge S.P.
Rated Volts / Phase | 460 / 3 |  | Total SP | 3.25
Rated Amperage / SF | 9.7/1.0 |  | System S.P. Set Point
|  |  | DX Coil P.D. | 0.29
Drive Data
Motor Sheave Size / Bore | BK65/1-7/8" |  | Final Filters P.D. | 0.30
Fan Sheave Size / Bore | 8"/1-5/8"
Belt CL Distance | 28.5
No. Belts / Size | 1/BX74 |  | Pre Filters P.D. | 0.4
|  |  | Total ESP | 2.50

## RTU-C01 VAV's
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C01 VAV's
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | TOTAL CFM
VAV-C101 | TABLES/SLOTS | REHEAT | 8 | 430 |  | 130 |  | 215 |  |  | 430
VAV-C102 | GP MGR/SLOTS | REHEAT | 6 | 355 |  | 145 |  | 180 |  |  | 355
VAV-C104 | GP/OPS OFFICE | REHEAT | 12 | 1075 |  | 375 |  | 625 |  |  | 1075
VAV-C105 | S BOOK | REHEAT | 6 | 250 |  | 75 |  | 125 |  |  | 250
VAV-C106 | MKTG WORK RM | REHEAT | 12 | 1295 |  | 375 |  | 625 |  |  | 1295
VAV-C107 | CONF RM | REHEAT | 6 | 325 |  | 130 |  | 165 |  |  | 325
VAV-C108 | OFFICE | REHEAT | 6 | 160 |  | 65 |  | 85 |  |  | 160
VAV-C110 | CR MGR/MKTG DIR | REHEAT | 6 | 360 |  | 145 |  | 180 |  |  | 360
VAV-C111 | IT MGR | REHEAT | 6 | 170 |  | 60 |  | 85 |  |  | 170
VAV-C112 | IT WORK RM/STOR | REHEAT | 12 | 1290 |  | 390 |  | 645 |  |  | 1290
VAV-C113 | IT SPVSR/NET ADMIN | REHEAT | 6 | 280 |  | 80 |  | 130 |  |  | 280
VAV-C114 | CORRIDOR | REHEAT | 8 | 465 |  | 140 |  | 235 |  |  | 465
VAV-C115 | OFFICE | REHEAT | 6 | 190 |  | 60 |  | 95 |  |  | 190 | Missing from submittal
|  |  |  | 6645 | 0 | 2170 | 0 | 3390 | 0

## RTU-C01 SGRD (1)
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C01 VAV SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
101-1 | 1g48 | A1 | 6X6 | 90 |  |  | 0
101-2 | 1g49 | A1 | 6X6 | 90 |  |  | 0
101-3 | 1g100 | A2 | 9X9 | 150 |  |  | 0
101-4 | S4 | D1 | 12X6 | 100 |  |  | 0
VAV-C101 |  |  |  | 430 |  | 0 | 0
102-1 | 1g50 | A2 | 9X9 | 140 |  |  | 0
102-2 | 1g52 | A2 | 9X9 | 115 |  |  | 0
102-3 | 1g51 | A1 | 6X6 | 100 |  |  | 0
VAV-C102 |  |  |  | 355 |  | 0 | 0
104-1 | 1g53 | A2 | 9X9 | 155 |  |  | 0
104-2 | 1g53 | A2 | 9X9 | 155 |  |  | 0
104-3 | 1g53 | A2 | 9X9 | 155 |  |  | 0
104-4 | 1g53 | A2 | 9X9 | 155 |  |  | 0
104-5 | 1g53 | A2 | 9X9 | 155 |  |  | 0
104-6 | 1g53 | A2 | 9X9 | 150 |  |  | 0
104-7 | 1g53 | A2 | 9X9 | 150 |  |  | 0
VAV-C104 |  |  |  | 1075 |  | 0 | 0
105-1 | 1g54 | A2 | 9X9 | 125 |  |  | 0
105-2 | 1g54 | A2 | 9X9 | 125 |  |  | 0
VAV-C105 |  |  |  | 250 |  | 0 | 0

## RTU-C01 SGRD (2)
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C01 VAV SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
106-1 | 1g55 | A2 | 9X9 | 150 |  |  | 0
106-2 | 1g55 | A2 | 9X9 | 165 |  |  | 0
106-3 | 1g55 | A2 | 9X9 | 165 |  |  | 0
106-4 | 1g55 | A2 | 9X9 | 165 |  |  | 0
106-5 | 1g55 | A2 | 9X9 | 165 |  |  | 0
106-6 | 1g55 | A2 | 9X9 | 165 |  |  | 0
106-7 | 1g55 | A2 | 9X9 | 160 |  |  | 0
106-8 | 1g55 | A2 | 9X9 | 160 |  |  | 0
VAV-C106 |  |  |  | 1295 |  | 0 | 0
107-1 | 1g57 | A2 | 9X9 | 165 |  |  | 0
107-2 | 1g57 | A2 | 9X9 | 160 |  |  | 0
VAV-C107 |  |  |  | 325 |  | 0 | 0
108-1 | 1g100 | A2 | 9X9 | 160 |  |  | 0
VAV-C108 |  |  |  | 160 |  | 0 | 0
110-1 | 1g100 | A2 | 9X9 | 150 |  |  | 0
110-2 | 1g59 | A1 | 6X6 | 100 |  |  | 0
110-3 | 1g58 | A2 | 9X9 | 110 |  |  | 0
VAV-C110 |  |  |  | 360 |  | 0 | 0
111-1 | 1g61 | A2 | 9X9 | 170 |  |  | 0
VAV-C111 |  |  |  | 170 |  | 0 | 0

## RTU-C01 SGRD (3)
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C01 VAV SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
112-1 | 1g62 | A2 | 9X9 | 175 |  |  | 0
112-2 | 1g64 | A1 | 6X6 | 50 |  |  | 0
112-3 | 1g62 | A2 | 9X9 | 180 |  |  | 0
112-4 | 1g62 | A2 | 9X9 | 175 |  |  | 0
112-5 | 1g62 | A2 | 9X9 | 175 |  |  | 0
112-6 | 1g62 | A2 | 9X9 | 175 |  |  | 0
112-7 | 1g62 | A2 | 9X9 | 180 |  |  | 0
112-8 | 1g62 | A2 | 9X9 | 180 |  |  | 0
VAV-C112 |  |  |  | 1290 |  | 0 | 0
113-1 | 1g60 | A2 | 9X9 | 170 |  |  | 0
113-2 | 1g65 | A2 | 9X9 | 110 |  |  | 0
VAV-C113 |  |  |  | 280 |  | 0 | 0
114-1 | 1g100 | A2 | 9X9 | 155 |  |  | 0
114-2 | 1g100 | A2 | 9X9 | 155 |  |  | 0
114-3 | 1g100 | A2 | 9X9 | 155 |  |  | 0
VAV-C114 |  |  |  | 465 |  | 0 | 0
115-1 | 1g52A | A1 | 66 | 95 |  |  | 0
115-2 | 1g52A | A1 | 66 | 95 |  |  | 0
VAV-C115 |  |  |  | 190 |  | 0 | 0

## RTU-C02
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C02 |  | Area: Area: CASINO BOH FLR 1
Supply Side
Unit Data |  |  | Test Data |  |  | USE FOR:
Manufacturer | DAIKIN |  |  | Design | Actual | VAV's
Model Number | MPS030FG4DV1 |  | Supply CFM | 8400 |  | No Return Fan
Serial Number | FBOU230400669 |  | Min OA CFM | 1915
Configuration | VERTICAL |  | Return CFM | 6485
No. Pre Filters / Size | 8 / 24X24X2 |  | Fan RPM | 1633 |  | Remove unused fields:
No. Pre Filters / Size |  |  | Operating HZ |  |  | Heat Wheel
No. Pre Filters / Size |  |  | RL Voltage | 460 |  | CW/HW Coil (Change to DX coil if applicable)
No. Final Filters / Size |  |  | RL Amperage | 13.0
No. Final Filters / Size |  |  | Motor B.H.P. | 7.4
No. Final Filters / Size
Performance Data
Motor Data X |  |  |  | Design | Actual
Motor MFG / Frame | BALDOR/215T |  | Suction S.P.
Horsepower / RPM | 10.0 / 1770 |  | Discharge S.P.
Rated Volts / Phase | 460 / 3 |  | Total SP | 3.38
Rated Amperage / SF | 12.5/1.0 |  | System S.P. Set Point
|  |  | DX Coil P.D. | 0.42
Drive Data
Motor Sheave Size / Bore | 8"/1-3/8" |  | Final Filters P.D. | 0.30
Fan Sheave Size / Bore | 9"/1-5/8"
Belt CL Distance | 28"
No. Belts / Size | 1/BX78 |  | Pre Filters P.D. | 0.07
|  |  | Total ESP | 2.40

## RTU-C02 VAV's
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C02 VAV's
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | TOTAL CFM
VAV-C201 | STOR/HOLDING | REHEAT | 6 | 180 |  | 65 |  | 90 |  |  | 180
VAV-C202 | BEV/SVC BAR | REHEAT | 14 | 2255 |  | 680 |  | 1130 |  |  | 2255
VAV-C203 | CHIP RM | REHEAT | 6 | 250 |  | 90 |  | 145 |  |  | 250
VAV-C204 | ADMIN/LD INSP | REHEAT | 6 | 180 |  | 65 |  | 90 |  |  | 180
VAV-C205 | TGC AGENT | REHEAT | 8 | 765 |  | 205 |  | 340 |  |  | 765 | Submittal Max is 680
VAV-C206 | TGC | REHEAT | 6 | 180 |  | 65 |  | 90 |  |  | 180
VAV-C207 | TGC | REHEAT | 6 | 180 |  | 65 |  | 90 |  |  | 180
VAV-C208 | WOMEN/MEN | REHEAT | 6 | 130 |  | 65 |  | 85 |  |  | 130
VAV-C209 | LOST/FOUND | REHEAT | 6 | 360 |  | 110 |  | 180 |  |  | 360
VAV-C210 | GM/ADMIN/POKER | REHEAT | 8 | 500 |  | 130 |  | 210 |  |  | 500 | Submittal Max is 420
VAV-C211 | DIR F&B/TRAINER | REHEAT | 6 | 295 |  | 90 |  | 150 |  |  | 295
VAV-C212 | F&B ADMIN | REHEAT | 12 | 1160 |  | 350 |  | 580 |  |  | 1060
VAV-C213 | COACHING | REHEAT | 6 | 265 |  | 110 |  | 135 |  |  | 265 | Submittal Max is 260
VAV-C215 | BEV MGR/R CHEF | REHEAT | 6 | 300 |  | 90 |  | 150 |  |  | 300
VAV-C216 | CASHIER | REHEAT | 8 | 470 |  | 145 |  | 235 |  |  | 470
VAV-C217 | EMP TRANS/STOR | REHEAT | 10 | 800 |  | 240 |  | 400 |  |  | 800
VAV-C218 | MEN/WOMEN | REHEAT | 8 | 425 |  | 130 |  | 215 |  |  | 425
|  |  |  | 8695 | 0 | 2695 | 0 | 4315 | 0

## RTU-C02 SGRD (1)
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C02 VAV SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
201-1 | 1g18 | A1 | 6X6 | 50 |  |  | 0
201-2 | 1g20 | A1 | 6X6 | 50 |  |  | 0
201-3 | 1g19 | B1 | 6X6 | 80 |  |  | 0
VAV-C201 |  |  |  | 180 |  | 0 | 0
202-1 | 1g16 | A2 | 9X9 | 225 |  |  | 0
202-2 | 1g16 | A2 | 9X9 | 225 |  |  | 0
202-3 | 1g16 | A2 | 9X9 | 225 |  |  | 0
202-4 | 1g16 | A2 | 9X9 | 225 |  |  | 0
202-5 | 1g16 | A2 | 9X9 | 225 |  |  | 0
202-6 | 1g16 | A2 | 9X9 | 225 |  |  | 0
202-7 | 1g16 | A2 | 9X9 | 225 |  |  | 0
202-8 | 1g16 | A2 | 9X9 | 225 |  |  | 0
202-9 | 1g16 | A2 | 9X9 | 230 |  |  | 0
202-10 | 1g16 | A2 | 9X9 | 225 |  |  | 0
VAV-C202 |  |  |  | 2255 |  | 0 | 0
203-1 | 1g21 | A2 | 9X9 | 125 |  |  | 0
203-2 | 1g21 | A2 | 9X9 | 125 |  |  | 0
VAV-C203 |  |  |  | 250 |  | 0 | 0
204-1 | 1g22 | A1 | 6X6 | 90 |  |  | 0
204-2 | 1g23 | A1 | 6X6 | 90 |  |  | 0
VAV-C204 |  |  |  | 180 |  | 0 | 0

## RTU-C02 SGRD (2)
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C02 VAV SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
205-1 | 1g24 | A2 | 9X9 | 130 |  |  | 0
205-2 | 1g24 | A2 | 9X9 | 130 |  |  | 0
205-3 | 1g24 | A2 | 9X9 | 130 |  |  | 0
205-4 | 1g24 | A2 | 9X9 | 125 |  |  | 0
205-5 | 1g24 | A2 | 9X9 | 125 |  |  | 0
205-6 | 1g24 | A2 | 9X9 | 125 |  |  | 0
VAV-C205 |  |  |  | 765 |  | 0 | 0
206-1 | 1g26 | A1 | 6X6 | 90 |  |  | 0
206-2 | 1g25 | A1 | 6X6 | 90 |  |  | 0
VAV-C206 |  |  |  | 180 |  | 0 | 0
207-1 | 1g28 | A1 | 6X6 | 90 |  |  | 0
207-2 | 1g27 | A1 | 6X6 | 90 |  |  | 0
VAV-C207 |  |  |  | 180 |  | 0 | 0
208-1 | 1g30 | A1 | 6X6 | 65 |  |  | 0
208-2 | 1g31 | A1 | 6X6 | 65 |  |  | 0
VAV-C208 |  |  |  | 130 |  | 0 | 0
209-1 | 1g29 | A1 | 6X6 | 105 |  |  | 0
209-2 | 1g29 | A1 | 6X6 | 105 |  |  | 0
209-3 | CORR | A2 | 9X9 | 150 |  |  | 0
VAV-C209 |  |  |  | 360 |  | 0 | 0
210-1 | 1g37 | A1 | 6X6 | 95 |  |  | 0
210-2 | 1g33 | A1 | 6X6 | 100 |  |  | 0
210-3 | 1g34 | A2 | 9X9 | 170 |  |  | 0
210-4 | 1g32 | A2 | 9X9 | 135 |  |  | 0
VAV-C210 |  |  |  | 500 |  | 0 | 0

## RTU-C02 SGRD (3)
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C02 VAV SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
211-1 | 1g41 | A1 | 6X6 | 100 |  |  | 0
211-2 | 1g39 | A1 | 6X6 | 90 |  |  | 0
211-3 | 1g38 | A1 | 6X6 | 105 |  |  | 0
VAV-C211 |  |  |  | 295 |  | 0 | 0
212-1 | 1g40 | A2 | 9X9 | 175 |  |  | 0
212-2 | 1g40 | A2 | 9X9 | 180 |  |  | 0
212-3 | 1g40 | A2 | 9X9 | 180 |  |  | 0
212-4 | 1g40 | A2 | 9X9 | 175 |  |  | 0
212-5 | 1g40 | A2 | 9X9 | 175 |  |  | 0
212-6 | 1g40 | A2 | 9X9 | 175 |  |  | 0
VAV-C212 |  |  |  | 1060 |  | 0 | 0
213-1 | 1g42 | A2 | 9X9 | 135 |  |  | 0
213-2 | 1g42 | A2 | 9X9 | 130 |  |  | 0
VAV-C13 |  |  |  | 265 |  | 0 | 0
215-1 | 1g45 | A2 | 9X9 | 110 |  |  | 0
215-2 | 1g44 | A1 | 6X6 | 100 |  |  | 0
215-3 | 1g43 | A1 | 6X6 | 90 |  |  | 0
VAV-C215 |  |  |  | 300 |  | 0 | 0
216-1 | 1g12 | E2 | 8 | 155 |  |  | 0
216-2 | 1g12 | E2 | 8 | 155 |  |  | 0
216-3 | 1g12 | E2 | 8 | 160 |  |  | 0
VAV-C216 |  |  |  | 470 |  | 0 | 0

## RTU-C02 SGRD (4)
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C02 VAV SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
217-1 | 1g11 | A2 | 9X9 | 165 |  |  | 0
217-2 | 1g11 | A2 | 9X9 | 165 |  |  | 0
217-3 | 1g11 | A2 | 9X9 | 165 |  |  | 0
217-4 |  | A1 | 6X6 | 40 |  |  | 0
217-5 | 1g01A | B1 | 6X6 | 100 |  |  | 0
217-6 | 1g11 | A2 | 9X9 | 165 |  |  | 0
VAV-C217 |  |  |  | 800 |  | 0 | 0
218-1 | 1g06 | E1 | 6 | 105 |  |  | 0
218-2 | 1g08 | E1 | 6 | 105 |  |  | 0
218-3 | 1g08 | E1 | 6 | 105 |  |  | 0
218-4 | 1g06 | E1 | 6 | 110 |  |  | 0
VAV-C218 |  |  |  | 425 |  | 0 | 0

## RTU-C03
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C03 |  | Area: CASINO BOH FLR 2
Supply Side
Unit Data |  |  | Test Data |  |  | USE FOR:
Manufacturer | DAIKIN |  |  | Design | Actual | VAV's
Model Number | MPS030FG4DV1 |  | Supply CFM | 9700 |  | No Return Fan
Serial Number | FBOU230400670 |  | Min OA CFM | 2900
Configuration | VERTICAL |  | Return CFM | 6800
No. Pre Filters / Size | 8 / 24X24X2 |  | Fan RPM | 1670 |  | Remove unused fields:
No. Pre Filters / Size |  |  | Operating HZ |  |  | Heat Wheel
No. Pre Filters / Size |  |  | RL Voltage | 460 |  | CW/HW Coil (Change to DX coil if applicable)
No. Final Filters / Size |  |  | RL Amperage | 13.0
No. Final Filters / Size |  |  | Motor B.H.P. | 7.8
No. Final Filters / Size
Performance Data
Motor Data X |  |  |  | Design | Actual
Motor MFG / Frame | BALDOR/215T |  | Suction S.P.
Horsepower / RPM | 10.0 / 1770 |  | Discharge S.P.
Rated Volts / Phase | 460 / 3 |  | Total SP | 3.16
Rated Amperage / SF | 12.5/1.0 |  | System S.P. Set Point
|  |  | DX Coil P.D. | 0.51
Drive Data
Motor Sheave Size / Bore | 7"/1-3/8" |  | Final Filters P.D. | 0.30
Fan Sheave Size / Bore | 8"/1-5/8"
Belt CL Distance | 28"
No. Belts / Size | 1/BX76 |  | Pre Filters P.D. | 0.10
|  |  | Total ESP | 2.0

## RTU-C03 VAV's
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C03 VAV's
Asset | Area Served | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max) | TOTAL CFM
VAV-C301 | PANTRY/CORR | REHEAT | 8 | 610 |  | 185 |  | 305 |  |  | 610
VAV-C302 | TCG LIC/WORK RM | REHEAT | 6 | 380 |  | 115 |  | 190 |  |  | 380
VAV-C303 | COMP TRAINING | REHEAT | 12 | 1125 |  | 340 |  | 565 |  |  | 1125
VAV-C304 | TABLE GAMES TRN | REHEAT | 14 | 2350 |  | 920 |  | 1150 |  |  | 2350 | Submittal Max is 2300
VAV-C305 | RECEPTION | REHEAT | 8 | 585 |  | 270 |  | 295 |  |  | 585
VAV-C306 | INTERVIEW | REHEAT | 6 | 105 |  | 65 |  | 85 |  |  | 105
VAV-C307 | RECRUITERS | REHEAT | 6 | 180 |  | 65 |  | 85 |  |  | 180
VAV-C308 | ER/BENEFITS | REHEAT | 6 | 270 |  | 85 |  | 135 |  |  | 270
VAV-C309 | NEW HIRE TRN | REHEAT | 12 | 1200 |  | 480 |  | 600 |  |  | 1200
VAV-C310 | HR WORK RM | REHEAT | 8 | 495 |  | 175 |  | 250 |  |  | 495
VAV-C311 | HR MGR/TRAINING | REHEAT | 6 | 220 |  | 65 |  | 105 |  |  | 220
VAV-C312 | EXEC OFC/TGCE | REHEAT | 6 | 260 |  | 65 |  | 105 |  |  | 260 | Submittal Max is 215
VAV-C313 | MENS/WOMENS | REHEAT | 6 | 130 |  | 65 |  | 85 |  |  | 130
VAV-C314 | CORRIDOR | REHEAT | 8 | 560 |  | 170 |  | 280 |  |  | 560 | Submittal Max is 555
VAV-C315 | RECEPT/OFFICE | REHEAT | 6 | 205 |  | 85 |  | 105 |  |  | 205
VAV-C316 | EXAM RM | REHEAT | 6 | 150 |  | 150 |  | 150 |  |  | 150
VAV-C317 | LAB RM | REHEAT | 6 | 200 |  | 200 |  | 200 |  |  | 200
VAV-C318 | UNIFORM STOR | REHEAT | 10 | 845 |  | 255 |  | 425 |  |  | 845

## RTU-C03 SGRD (1)
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C03 VAV SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
301-1 | CORR | A1 | 6X6 | 100 |  |  | 0
301-2 | 2g02 | A2 | 9X9 | 115 |  |  | 0
301-3 | 2g01 | A1 | 6X6 | 80 |  |  | 0
301-4 | 2g02 | A2 | 9X9 | 115 |  |  | 0
301-5 | 2g06 | A1 | 6X6 | 100 |  |  | 0
301-6 | 2g06 | A1 | 6X6 | 100 |  |  | 0
VAV-C301 |  |  |  | 610 |  | 0 | 0
302-1 | 2g03A | A2 | 9X9 | 185 |  |  | 0
302-2 | 2g03 | A2 | 9X9 | 195 |  |  | 0
VAV-C302 |  |  |  | 380 |  | 0 | 0
303-1 | 2g07 | A2 | 9X9 | 185 |  |  | 0
303-2 | 2g07 | A2 | 9X9 | 185 |  |  | 0
303-3 | 2g07 | A2 | 9X9 | 185 |  |  | 0
303-4 | 2g07 | A2 | 9X9 | 190 |  |  | 0
303-5 | 2g07 | A2 | 9X9 | 190 |  |  | 0
303-6 | 2g07 | A2 | 9X9 | 190 |  |  | 0
VAV-C303 |  |  |  | 1125 |  | 0 | 0
304-1 | 2g05 | A2 | 9X9 | 230 |  |  | 0
304-2 | 2g05 | A2 | 9X9 | 230 |  |  | 0
304-3 | 2g05 | A2 | 9X9 | 230 |  |  | 0
304-4 | 2g05 | A2 | 9X9 | 230 |  |  | 0
304-5 | 2g05 | A2 | 9X9 | 230 |  |  | 0
304-6 | 2g05 | A2 | 9X9 | 230 |  |  | 0
304-7 | 2g05 | A2 | 9X9 | 230 |  |  | 0
304-8 | 2g05 | A2 | 9X9 | 230 |  |  | 0
304-9 | 2g04 | A1 | 6X6 | 50 |  |  | 0
304-10 | 2g05 | A2 | 9X9 | 230 |  |  | 0
304-11 | 2g05 | A2 | 9X9 | 230 |  |  | 0
VAV-C304 |  |  |  | 2350 |  | 0 | 0

## RTU-C03 SGRD (2)
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C03 VAV SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
305-1 | 2g08 | A2 | 9X9 | 115 |  |  | 0
305-2 | 2g08 | A2 | 9X9 | 115 |  |  | 0
305-3 | 2g08A | A2 | 9X9 | 115 |  |  | 0
305-4 | 2g08 | A2 | 9X9 | 120 |  |  | 0
305-5 | 2g08 | A2 | 9X9 | 120 |  |  | 0
VAV-C305 |  |  |  | 585 |  | 0 | 0
306-1 | INTERVIEW | A1 | 6X6 | 105 |  |  | 0
VAV-C306 |  |  |  | 105 |  | 0 | 0
307-1 |  | A1 | 6X6 | 90 |  |  | 0
307-2 |  | A1 | 6X6 | 90 |  |  | 0
VAV-C307 |  |  |  | 180 |  | 0 | 0
308-1 | 2g14 | A1 | 6X6 | 90 |  |  | 0
308-2 | 2g13 | A1 | 6X6 | 90 |  |  | 0
308-3 | 2g11 | A1 | 6X6 | 90 |  |  | 0
VAV-C308 |  |  |  | 270 |  | 0 | 0
309-1 | 2g21 | A2 | 9X9 | 200 |  |  | 0
309-2 | 2g21 | A2 | 9X9 | 200 |  |  | 0
309-3 | 2g21 | A2 | 9X9 | 200 |  |  | 0
309-4 | 2g21 | A2 | 9X9 | 200 |  |  | 0
309-5 | 2g21 | A2 | 9X9 | 200 |  |  | 0
309-6 | 2g21 | A2 | 9X9 | 200 |  |  | 0
VAV-C309 |  |  |  | 1200 |  | 0 | 0
310-1 | 2g20A | A2 | 9X9 | 190 |  |  | 0
310-2 | 2g20A | A2 | 9X9 | 190 |  |  | 0
310-3 | CORR | A1 | 6X6 | 60 |  |  | 0
310-4 | CORR | A1 | 6X6 | 55 |  |  | 0
VAV-C310 |  |  |  | 495 |  | 0 | 0

## RTU-C03 SGRD (3)
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C03 VAV SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
311-1 | 2g18 | A2 | 9X9 | 115 |  |  | 0
311-2 | 2g18b | A1 | 6X6 | 105 |  |  | 0
VAV-C311 |  |  |  | 220 |  | 0 | 0
312-1 | 2g15 | A1 | 6X6 | 50 |  |  | 0
312-2 | 2g17 | A1 | 6X6 | 105 |  |  | 0
312-3 | 2g16 | A1 | 6X6 | 105 |  |  | 0
VAV-312 |  |  |  | 260 |  | 0 | 0
313-1 | 2g23 | A1 | 6X6 | 65 |  |  | 0
313-2 | 2g22 | A1 | 6X6 | 65 |  |  | 0
VAV-C313 |  |  |  | 130 |  | 0 | 0
314-1 | 2g25 | A2 | 9X9 | 150 |  |  | 0
314-2 | 2g25 | A2 | 9X9 | 110 |  |  | 0
314-3 | 2g25 | A2 | 9X9 | 150 |  |  | 0
314-4 | 2g25 | A2 | 9X9 | 150 |  |  | 0
VAV-314 |  |  |  | 560 |  | 0 | 0
315-1 |  | A1 | 6X6 | 100 |  |  | 0
315-2 |  | A1 | 6X6 | 105 |  |  | 0
VAV-C315 |  |  |  | 205 |  | 0 | 0
316-1 | 2g27 | A2 | 9X9 | 150 |  |  | 0
VAV-C316 |  |  |  | 150 |  | 0 | 0
317-1 | 2g29 | A2 | 9X9 | 200 |  |  | 0
VAV-C317 |  |  |  | 200 |  | 0 | 0

## RTU-C03 SGRD (4)
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C03 VAV SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
318-1 | 2g33 | A2 | 9X9 | 130 |  |  | 0
318-2 | 2g33 | A2 | 9X9 | 130 |  |  | 0
318-3 | 2g33 | A2 | 9X9 | 130 |  |  | 0
318-4 | 2g33 | A2 | 9X9 | 130 |  |  | 0
318-5 | 2g33 | A1 | 6X6 | 100 |  |  | 0
318-6 | 2g33 | A1 | 6X6 | 100 |  |  | 0
318-7 | 2g33 | A2 | 9X9 | 125 |  |  | 0
VAV-C318 |  |  |  | 845 |  | 0 | 0

## RTU-C04
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C04 |  | Area: CASINO BAR
Supply Side
Unit Data
Manufacturer | DAIKIN
Model Number | DPS015AHMC4DW
Serial Number | 5LPV230906245
Configuration | VERTICAL
No. Pre Filters / Size | 6 / 18X24X2
No. Pre Filters / Size | 6 / 18X24X4
No. Pre Filters / Size
No. Final Filters / Size
No. Final Filters / Size
No. Final Filters / Size
Motor Data X
Motor MFG / Frame | DAIKEN/NL
Horsepower / RPM | 8.0 / 2600
Rated Volts / Phase | 480 / 3
Rated Amperage / SF | 6.8 / NL
Test Data
| Design | Actual
Supply CFM | 3800
Min OA CFM | 1630
Return CFM | 2170
Fan RPM | 1693
Operating HZ
RL Voltage | 460
RL Amperage | 6.8
Motor B.H.P. | 1.67
Performance Data
| Design | Actual
Suction S.P.
Discharge S.P.
Total SP | 1.81
Final Filters P.D.
DX Coil P.D.
Gas Reheat P.D.
Gas Heat P.D.
Pre Filters P.D.
Total ESP

## RTU-C04 SGRD
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C04 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
4-1 | 1468 | F1 | 8 | 230 |  |  | 0
4-2 | 1468 | F1 | 8 | 230 |  |  | 0
4-3 | 1468 | F1 | 8 | 230 |  |  | 0
4-4 | 1g15 | D2 | 16X8 | 605 |  |  | 0
4-5 | 1468 | F1 | 8 | 230 |  |  | 0
4-6 | 1g15 | D2 | 16X8 | 605 |  |  | 0
4-7 | 1g15 | D2 | 16X8 | 605 |  |  | 0
4-8 | 1468 | F1 | 8 | 230 |  |  | 0
4-9 | 1468 | F1 | 8 | 230 |  |  | 0
4-10 | 1g15 | D2 | 16X8 | 605 |  |  | 0
|  |  |  | 3800 |  | 0 | 0

## RTU-C05
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C05 |  | Area: CASINO CONNECTOR
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | DAIKIN |  | Manufacturer | DAIKIN
Model Number | DPSA020A4BHCMDA |  | Model Number | DPSA020
Serial Number | FBOU23070442 |  | Serial Number
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 8 / 20X24X2 |  | No. Pre Filters / Size
No. Pre Filters / Size | 4 / 24X24X4 |  | No. Pre Filters / Size
No. Pre Filters / Size |  |  | No. Pre Filters / Size
No. Final Filters / Size
No. Final Filters / Size
No. Final Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | 2X DAIKEN |  | Motor MFG / Frame
Horsepower / RPM | 2@ 5200W / NL |  | Horsepower / RPM | 5.3 /
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 2@ 7.9 / 1 |  | Rated Amperage / SF | 5.7
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Supply CFM | 6400 |  | Total CFM | 6400
Min OA CFM | 1050 |  | Fan RPM | 1152
Return CFM | 5350 |  | Operating HZ
Fan RPM | 1677 |  | RL Voltage | 460
Operating HZ |  |  | RL Amperage | 5.7
RL Voltage | 460 |  | Motor B.H.P. | 1.35
RL Amperage | 2@ 7.9
Motor B.H.P. | 3.34
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 2.13 |  | Total SP
Final Filters P.D. | 0.04
DX Coil P.D. | 0.40
Gas Reheat P.D. | 0.06
Gas Heat P.D. | 0.03 |  | Pre Filters P.D.
Pre Filters P.D. | 0.05
Total ESP | 1.5 |  | Total ESP | 0.8

## RTU-C05 SGRD
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C05 SUPPLY
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
5-1 | 1g46 | F1 | 8 | 150 |  |  | 0
5-2 | 1g46 | F1 | 8 | 150 |  |  | 0
5-3 | 1g46 | F1 | 8 | 150 |  |  | 0
5-4 | 1g46 | F1 | 8 | 150 |  |  | 0
5-5 | 1g46 | F1 | 8 | 150 |  |  | 0
5-6 | 1g46 | F1 | 8 | 150 |  |  | 0
5-7 | 1g46 | F1 | 8 | 150 |  |  | 0
5-8 | 1g46 | D1 | 12X6 | 120 |  |  | 0
5-9 | 1h04 | D2 | 16X8 | 550 |  |  | 0
5-10 | 1g46 | F1 | 8 | 250 |  |  | 0
5-11 | 1g46 | F1 | 8 | 250 |  |  | 0
5-12 | 1g46 | F1 | 8 | 250 |  |  | 0
5-13 | 1g46 | F1 | 8 | 250 |  |  | 0
5-14 | 1g46 | F1 | 8 | 250 |  |  | 0
5-15 | 1h02 | F1 | 8 | 230 |  |  | 0
5-16 | 1h02 | F1 | 8 | 230 |  |  | 0
5-17 | 1h02 | F1 | 8 | 230 |  |  | 0
5-18 | 1h02 | F1 | 8 | 230 |  |  | 0
5-19 | 1h02 | F1 | 8 | 230 |  |  | 0
5-20 | 1h02 | D2 | 16X8 | 570 |  |  | 0
5-21 | 1h02 | D2 | 16X8 | 570 |  |  | 0
5-22 | 1h02 | D2 | 16X8 | 570 |  |  | 0
5-23 | 1h02 | D2 | 16X8 | 570 |  |  | 0
|  |  |  | 6400 |  | 0 | 0

## RTU-C06
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C06 |  | Area: POKER / GAMING
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | DAIKIN |  | Manufacturer | DAIKIN
Model Number | MPS035FG4DV1 |  | Model Number | MPS035F
Serial Number | FBOU230400671 |  | Serial Number | N/A
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 8 / 24X24X2 |  | No. Pre Filters / Size | 3 / 24X24X2
No. HW Pre Filters / Size | 3 / 24X24X2 |  | No. Pre Filters / Size
No. Pre Filters / Size |  |  | No. Pre Filters / Size
No. Final Filters / Size
No. Final Filters / Size
No. Final Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR/254T |  | Motor MFG / Frame | EBM PAPST / NL
Horsepower / RPM | 15.0 / 1770 |  | Horsepower / RPM | 5030W / 1750
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 18.2 / 1.15 |  | Rated Amperage / SF | 6.1 / NL
Drive Data
Motor Sheave Size / Bore | 7.5"/1-5/8"
Fan Sheave Size / Bore | 6.5"/1-5/8"
Belt CL Distance | 28.5"
No. Belts / Size | 1/5VX780
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Supply CFM | 11000 | 11586 | Total CFM | 3500 | 3567
Min OA CFM | 3850 | 4047 | Fan RPM | 1800
Return CFM | 7150 | 7539 | Operating % |  | 64
Fan RPM | 1899 | 1661 | RL Voltage | 460 | 479/476/476
Operating HZ |  | 48HZ | RL Amperage | 6.1 | 1.9/2.1/1.9
RL Voltage | 460 | 332 VFD | Motor B.H.P.
RL Amperage | 17.7 | 10.9 VFD
Motor B.H.P. | 11.3 | 6.6
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  | -1.26 | Suction S.P. |  | -1.21
Discharge S.P. |  | 0.85 | Discharge S.P. |  | 0.05
Total SP | 4.05 | 2.11 | Total SP |  | 1.26
OA Flow Gain |  | 1.72
Final Filters P.D. | 0.30 | 0.10
Heat Wheel P.D. | 0.59 | 0.41
DX Coil P.D. | 0.59 | * COMBINED | Heat Wheel P.D. | 0.50 | 0.52
Gas Reheat P.D. | 0.11 | 0.46 | Pre Filters P.D. |  | 0.01
Pre Filters P.D. | 0.13 | 0.13
Total ESP | 1.6 | 1.55 | Total ESP | 1.0 | 0.75
MA |  | -0.7
*MIN OA DAMPER 73%

## RTU-C06 SGRD
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C06 SUPPLY (UNDERFLOOR)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
6-1 | CASINO FLR | DUCT | 36X18 | 5500 | 7661 | 5873 | 1.0678
6-2 | CASINO FLR | DUCT | 36X18 | 5500 | 7452 | 5713 | 1.0387
|  |  |  | 11000 |  | 11586 | 1.0533

## RTU-C07
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C07 |  | Area: POKER / GAMING
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | DAIKIN |  | Manufacturer | DAIKIN
Model Number | MPS035FG4DV1CB |  | Model Number | MPS035F
Serial Number | FBOU230400672 |  | Serial Number | NL
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 8 / 24X24X2 |  | No. Pre Filters / Size | 3 / 24X24X2
No. HW Pre Filters / Size | 3 / 24X24X2 |  | No. Pre Filters / Size
No. Pre Filters / Size |  |  | No. Pre Filters / Size
No. Final Filters / Size
No. Final Filters / Size
No. Final Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR/254T |  | Motor MFG / Frame | EBM PAPST / NL
Horsepower / RPM | 15.0 / 1770 |  | Horsepower / RPM | 5030W / 1750
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 18.2 / 1.15 |  | Rated Amperage / SF | 6.1 / NL
Drive Data
Motor Sheave Size / Bore | 7.5" / 1-5/8"
Fan Sheave Size / Bore | 6.5" / 1-5/8"
Belt CL Distance | 28.5"
No. Belts / Size | 1 / 5VX780
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Supply CFM | 11000 | 11294 | Total CFM | 3500 | 3514
Min OA CFM | 3850 | 4047 | Fan RPM | 1800
Return CFM | 7150 | 7247 | Operating % |  | 56%
Fan RPM | 1899 | 1604 | RL Voltage | 460 | 481/476/477
Operating HZ |  | 46.5HZ | RL Amperage | 6.1 | 1.4/1.6/1.3
RL Voltage | 460 | 318 | Motor B.H.P.
RL Amperage | 17.7 | 10.6
Motor B.H.P. | 11.3 | 6.13
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  | -1.21 | Suction S.P. |  | -0.88
Discharge S.P. |  | 0.78 | Discharge S.P. |  | 0.04
Total SP | 4.05 | 1.99 | Total SP |  | 0.92
Final Filters P.D. | 0.30 | 0.01
DX Coil P.D. | 0.59 | * COMBINED
Gas Reheat P.D. | 0.11 | *0.55 | Heat Wheel P.D. | 0.50 | 0.51
Heat Wheel P.D. |  | 0.36 | Pre Filters P.D. |  | 0.21
Pre Filters P.D. | 0.13 | 0.14
Total ESP | 1.6 | 1.43 | Total ESP | 1.0 | 0.66

## RTU-C07 SGRD
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C07 SUPPLY (UNDERFLOOR)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
7-1 | CASINO FLR | DUCT | 36X18 | 5500 | 5715 | 5472 | 0.99491
7-2 | CASINO FLR | DUCT | 36X18 | 5500 | 6084 | 5822 | 1.0585
|  |  |  | 11000 |  | 11294 | 1.0267

## RTU-C08
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C08 |  | Area: POKER / GAMING
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | DAIKIN |  | Manufacturer | DAIKIN
Model Number | MPS035FG4DV1CB |  | Model Number | MPS035F
Serial Number | FBOU230400673 |  | Serial Number | NL
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 8 / 24X24X2 |  | No. Pre Filters / Size | 3 / 24X24X2
No. HW Pre Filters / Size | 3 / 24X24X2 |  | No. Pre Filters / Size
No. Pre Filters / Size |  |  | No. Pre Filters / Size
No. Final Filters / Size
No. Final Filters / Size
No. Final Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR/254T |  | Motor MFG / Frame | EBM PAPST / NL
Horsepower / RPM | 15.0 / 1770 |  | Horsepower / RPM | 5030W / 1750
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 18.2 / 1.15 |  | Rated Amperage / SF | 6.1 / NL
Drive Data
Motor Sheave Size / Bore | 7.5" / 1-5/8"
Fan Sheave Size / Bore | 6.5" / 1-5/8"
Belt CL Distance | 28.5"
No. Belts / Size | 1 / 5VX780
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Supply CFM | 11000 | 10989 | Total CFM | 3500 | 3464
Min OA CFM | 3850 | 3959 | Fan RPM | 1800
Return CFM | 7150 | 7030 | Operating % |  | 70%
Fan RPM | 1899 | 1644 | RL Voltage | 460 | 480/477/475
Operating HZ |  | 47.5 | RL Amperage | 6.1 | 2.1/2.5/2.4
RL Voltage | 460 | 327 VFD | Motor B.H.P.
RL Amperage | 17.7 | 10.7 VFD
Motor B.H.P. | 11.3 | 6.3
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  | -1.26 | Suction S.P. |  | -1.12
|  | 0.76 | Discharge S.P. |  | 0.03
Total SP | 4.05 | 2.02 | Total SP |  | 1.15
OA Flow Gain |  | 1.57
Final Filters P.D. | 0.30 | 0.01
DX Coil P.D. | 0.59 | COMBINED*
Gas Reheat P.D. | 0.11 | *0.53 | Heat Wheel P.D. | 0.50 | 0.49
Heat Wheel P.D. | 0.19 | 0.40 | Pre Filters P.D. |  | 0.06
Pre Filters P.D. | 0.13 | 0.13
Total ESP | 1.6 | 1.48 | Total ESP | 1.0 | 0.75
MA |  | -0.72
OA DAMPER POS. |  | 70%

## RTU-C08 SGRD
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C08 SUPPLY (UNDERFLOOR)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
8-1 | CASINO FLR | DUCT | 24X18 | 3100 | 3021 | 3021 | 0.97452
8-2 | CASINO FLR | DUCT | 20X18 | 2400 | 2811 | 2811 | 1.1712 | *NO DAMPER
8-3 | CASINO FLR | DUCT | 36X18 | 5500 | 5157 | 5157 | 0.93764
|  |  |  | 11000 |  | 10989 | 0.999

## RTU-C09
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C09 |  | Area: POKER / GAMING
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | DAIKIN |  | Manufacturer | DAIKIN
Model Number | MPS035FG4DV1CBS |  | Model Number | MPS035F
Serial Number | FBOU230400674 |  | Serial Number | NL
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 8 / 24X24X2 |  | No. Pre Filters / Size | 3 / 24X24X2
No. Pre Filters / Size | 3 / 24X24X2 |  | No. Pre Filters / Size
No. Pre Filters / Size |  |  | No. Pre Filters / Size
No. Final Filters / Size
No. Final Filters / Size
No. Final Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR/254T |  | Motor MFG / Frame | EBM PAPST / NL
Horsepower / RPM | 15.0 / 1770 |  | Horsepower / RPM | 5030W / 1750
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 18.2 / 1.15 |  | Rated Amperage / SF | 6.1 / NL
Drive Data
Motor Sheave Size / Bore | 7.5" / 1-5/8"
Fan Sheave Size / Bore | 6.5" / 1-5/8"
Belt CL Distance | 28.5"
No. Belts / Size | 1 / 5VX780
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Supply CFM | 11000 | 11335 | Total CFM | 3500 | 3518
Min OA CFM | 3850 | 3884 | Fan RPM | 1800
Return CFM | 7150 | 7454 | Operating % |  | 68
Fan RPM | 1899 | 1656 | RL Voltage | 460 | 479/477/476
Operating HZ |  | 48 | RL Amperage | 6.1 | 2.4/2.1/2.3
RL Voltage | 460 | 332 VFD | Motor B.H.P.
RL Amperage | 17.7 | 10.9VFD
Motor B.H.P. | 11.3 | 6.6
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  | -1.23 | Suction S.P. |  | -1.25
Discharge S.P. |  | 0.78 | Discharge S.P. |  | 0.02
Total SP | 4.05 | 2.01 | Total SP |  | 1.27
OA Gain |  | 1.85
Final Filters P.D. | 0.30 | 0.10
DX Coil P.D. | 0.59 | COMBINED*
Gas Reheat P.D. | 0.11 | *0.58 | Heat Wheel P.D. | 0.50 | 0.51
Heat Wheel P.D. | 0.19 | 0.42 | Pre Filters P.D. |  | 0.19
Pre Filters P.D. | 0.13 | 0.12
Total ESP | 1.6 | 1.33 | Total ESP | 1.0 | 0.57
MA |  | -0.55
OA DAMPER POS. |  | 60%

## RTU-C09 SGRD
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C09 SUPPLY (UNDERFLOOR)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
9-1 | CASINO FLR | DUCT | 36X18 | 5500 | 10435 | 5868 | 1.0669
9-2 | CASINO FLR | DUCT | 36X18 | 5500 | 738 | 5467 | 0.994
|  |  |  | 11000 |  | 11335 | 1.0305

## RTU-C10
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C10 |  | Area: POKER / GAMING
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | DAIKIN |  | Manufacturer | DAIKIN
Model Number | MPS035FG4DV1CB |  | Model Number | MPS035F
Serial Number | FBOU230400675 |  | Serial Number | NL
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 8 / 24X24X2 |  | No. Pre Filters / Size | 3 / 24X24X2
No. Pre Filters / Size | 3 / 24X24X2 |  | No. Pre Filters / Size
No. Pre Filters / Size |  |  | No. Pre Filters / Size
No. Final Filters / Size
No. Final Filters / Size
No. Final Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR/254T |  | Motor MFG / Frame | EBM PAPST / NL
Horsepower / RPM | 15.0 / 1770 |  | Horsepower / RPM | 5030W / 1750
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 18.2 / 1.15 |  | Rated Amperage / SF | 6.1 / NL
Drive Data
Motor Sheave Size / Bore | 7.5" / 1-5/8"
Fan Sheave Size / Bore | 6.5" / 1-5/8"
Belt CL Distance | 28.5"
No. Belts / Size | 1 / 5VX780
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Supply CFM | 11000 | 11404 | Total CFM | 3500
Min OA CFM | 3850 |  | Fan RPM | 1800
Return CFM | 7150 |  | Operating HZ
Fan RPM | 1899 |  | RL Voltage | 460
Operating HZ |  | 47 | RL Amperage | 6.1
RL Voltage | 460 |  | Motor B.H.P.
RL Amperage | 17.7
Motor B.H.P. | 11.3
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 4.05 |  | Total SP
OA Gain
Final Filters P.D. | 0.30
DX Coil P.D. | 0.59 | COMBINED*
Gas Reheat P.D. | 0.11 | * | Heat Wheel P.D. | 0.50
Heat Wheel P.D. | 0.19 |  | Pre Filters P.D.
Pre Filters P.D. | 0.13
Total ESP | 1.6 |  | Total ESP | 1.0

## RTU-C10 SGRD
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C10 SUPPLY (UNDERFLOOR)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
10-1 | CASINO FLR | DUCT | 36X18 | 5500 | 5855 | 5733 | 1.0424
10-2 | CASINO FLR | DUCT | 36X18 | 5500 | 5792 | 5671 | 1.0311
|  |  |  | 11000 |  | 11404 | 1.0367

## RTU-C11
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C11 |  | Area: POKER / GAMING
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | DAIKIN |  | Manufacturer | DAIKIN
Model Number | MPS035FG4DV1CBS |  | Model Number | MPS035F
Serial Number | FBOU230400676 |  | Serial Number | NL
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 8 / 24X24X2 |  | No. Pre Filters / Size | 3 / 24X24X2
No. Pre Filters / Size | 3 / 24X24X2 |  | No. Pre Filters / Size
No. Pre Filters / Size |  |  | No. Pre Filters / Size
No. Final Filters / Size
No. Final Filters / Size
No. Final Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR/254T |  | Motor MFG / Frame | EBM PAPST / NL
Horsepower / RPM | 15.0 / 1770 |  | Horsepower / RPM | 5030W / 1750
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 18.2 / 1.15 |  | Rated Amperage / SF | 6.1 / NL
Drive Data
Motor Sheave Size / Bore | 7.5" / 1-5/8"
Fan Sheave Size / Bore | 6.5" / 1-5/8"
Belt CL Distance | 28.5"
No. Belts / Size | 1 / 5VX780
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Supply CFM | 11000 | 10965 | Total CFM | 3500 | 3541
Min OA CFM | 3850 | 3820 | Fan RPM | 1800
Return CFM | 7150 | 7145 | Operating % |  | 62%
Fan RPM | 1899 | 1762 | RL Voltage | 460 | 481/478/477
Operating HZ |  | 51.1 | RL Amperage | 6.1 | 1.7/2.0/1.9
RL Voltage | 460 | 363 VFD | Motor B.H.P.
RL Amperage | 17.7 | 9.3 VFD
Motor B.H.P. | 11.3 | 5.3
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  | -1.14 | Suction S.P. |  | -0.86
Discharge S.P. |  | 0.65 | Discharge S.P. |  | 0.02
Total SP | 4.05 | 1.79 | Total SP |  | 0.88
OA Gain |  | 1.36
Final Filters P.D. | 0.30 | 0.01
DX Coil P.D. | 0.59 | COMBINED*
Gas Reheat P.D. | 0.11 | *0.45 | Heat Wheel P.D. | 0.50 | 0.51
Heat Wheel P.D. | 0.19 | 0.44 | Pre Filters P.D. |  | 0.32
Pre Filters P.D. | 0.13 | 0.11
Total ESP | 1.6 | 1.33 | Total ESP | 1.0 | 0.70
MA |  | -0.68
OA DAMPER TESTED AT 76%

## RTU-C11 SGRD
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C11 SUPPLY (UNDERFLOOR)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
11-1 | CASINO FLR | DUCT | 36X18 | 5500 | 5386 | 5672 | 1.0313
11-2 | CASINO FLR | DUCT | 36X18 | 5500 | 5027 | 5293 | 0.96236
|  |  |  | 11000 |  | 10965 | 0.99682

## RTU-C12
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C12 |  | Area: POKER / GAMING
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | DAIKIN |  | Manufacturer | DAIKIN
Model Number | MPS035FG4DV1CBS |  | Model Number | MPS035F
Serial Number | FBOU230400677 |  | Serial Number | NL
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 8 / 24X24X2 |  | No. Pre Filters / Size | 3 / 24X24X2
No. Pre Filters / Size | 3 / 24X24X2 |  | No. Pre Filters / Size
No. Pre Filters / Size |  |  | No. Pre Filters / Size
No. Final Filters / Size
No. Final Filters / Size
No. Final Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR/254T |  | Motor MFG / Frame | EBM PAPST / NL
Horsepower / RPM | 15.0 / 1770 |  | Horsepower / RPM | 5030W / 1750
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 18.2 / 1.15 |  | Rated Amperage / SF | 6.1 / NL
Drive Data
Motor Sheave Size / Bore | 7.5" / 1-5/8"
Fan Sheave Size / Bore | 6.5" / 1-5/8"
Belt CL Distance | 28.5"
No. Belts / Size | 1 / 5VX780
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Supply CFM | 11000 | 11003 | Total CFM | 3500 | 3520
Min OA CFM | 3850 | 3898 | Fan RPM | 1800
Return CFM | 7150 | 7105 | Operating % |  | 63
Fan RPM | 1899 | 1855 | RL Voltage | 460 | 483/480/478
Operating HZ |  | 53.8 | RL Amperage | 6.1 | 1.9/1.7/2.1
RL Voltage | 460 | 394VFD | Motor B.H.P.
RL Amperage | 17.7 | 9.5VFD
Motor B.H.P. | 11.3 | 5.7
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  | -1.26 | Suction S.P. |  | -0.87
Discharge S.P. |  | 0.67 | Discharge S.P. |  | 0.04
Total SP | 4.05 | 1.93 | Total SP |  | 0.91
OA Gain |  | 1.33
Final Filters P.D. | 0.30 | 0.13
DX Coil P.D. | 0.59 | COMBINED*
Gas Reheat P.D. | 0.11 | *0.27 | Heat Wheel P.D. | 0.50 | 0.51
Heat Wheel P.D. | 0.19 | 0.48 | Pre Filters P.D. |  | 0.50
Pre Filters P.D. | 0.13 | 0.13
Total ESP | 1.6 | 1.53 | Total ESP | 1.0 | 0.90
MA |  | -0.86
OA FLOW TESTED AT 74% DAMPER

## RTU-C12 SGRD
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C12 SUPPLY (UNDERFLOOR)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
12-1 | CASINO FLR | DUCT | 36X18 | 2750 | 2556 | 2681 | 0.97491
12-2 | CASINO FLR | DUCT | 36X18 | 2750 | 2547 | 2670 | 0.97091
12-3 | CASINO FLR | DUCT | 36X18 | 2750 | 909 | 2795 | 1.0164
12-4 | CASINO FLR | DUCT | 36X18 | 2750 | 4059 | 2857 | 1.0389
|  |  |  | 11000 |  | 11003 | 1.0003

## RTU-C13
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C13 |  | Area: POKER / GAMING
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | DAIKIN |  | Manufacturer | DAIKIN
Model Number | MPS035FG4DV1CBS |  | Model Number | MPS035F
Serial Number | FBOU230400678 |  | Serial Number | NL
Configuration | VERTICAL |  | Configuration | VERTICAL
No. Pre Filters / Size | 8 / 24X24X2 |  | No. Pre Filters / Size | 3 / 24X24X2
No. Pre Filters / Size | 3 / 24X24X2 |  | No. Pre Filters / Size
No. Pre Filters / Size |  |  | No. Pre Filters / Size
No. Final Filters / Size
No. Final Filters / Size
No. Final Filters / Size
Motor Data X |  |  | Motor Data X
Motor MFG / Frame | BALDOR/254T |  | Motor MFG / Frame | EBM PAPST / NL
Horsepower / RPM | 15.0 / 1770 |  | Horsepower / RPM | 5030W / 1750
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF | 18.2 / 1.15 |  | Rated Amperage / SF | 6.1 / NL
Drive Data
Motor Sheave Size / Bore | 7.5" / 1-5/8"
Fan Sheave Size / Bore | 6.5" / 1-5/8"
Belt CL Distance | 28.5"
No. Belts / Size | 1 / 5VX780
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Supply CFM | 11000 | 11403 | Total CFM | 3500 | 3515
Min OA CFM | 3850 | 3997 | Fan RPM | 1800
Return CFM | 7150 | 7406 | Operating % |  | 65
Fan RPM | 1899 | 1710 | RL Voltage | 460 | 482/480/479
Operating HZ |  | 49.6 | RL Amperage | 6.1 | 2.1/1.8/2.0
RL Voltage | 460 | 348VFD | Motor B.H.P.
RL Amperage | 17.7 | 11.5VFD
Motor B.H.P. | 11.3 | 7.3
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  | -1.33 | Suction S.P. |  | -0.97
Discharge S.P. |  | 0.77 | Discharge S.P. |  | 0.03
Total SP | 4.05 | 2.10 | Total SP |  | 1.00
OA Gain |  | 1.77
Final Filters P.D. | 0.30 | 0.06
DX Coil P.D. | 0.59 | COMBINED*
Gas Reheat P.D. | 0.11 | *0.67 | Heat Wheel P.D. | 0.50 | 0.50
Heat Wheel P.D. | 0.19 | 0.43 | Pre Filters P.D. |  | 0.13
Pre Filters P.D. | 0.13 | 0.12
Total ESP | 1.6 | 1.37 | Total ESP | 1.0 | 0.63
MA |  | -0.6

## RTU-C13 SGRD
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: RTU-C13 SUPPLY (UNDERFLOOR)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
13-1 | CASINO FLR | DUCT | 36X18 | 5500 | 3397 | 5683 | 1.0333
13-2 | CASINO FLR | DUCT | 36X18 | 5500 | 8006 | 5720 | 1.04
|  |  |  | 11000 |  | 11403 | 1.0366

## VRF-C01
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-C01 |  | Area: CASINO FLR 1 ELEV LOBBY
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual
Model Num | FXSQ18TBVJU |  |  |  | SA CFM | 600
Serial Num |  |  |  |  | Fan RPM
[5 empty] | OA CFM | 85
[5 empty] | RA CFM | 515
Motor Data |  |  |  |  | RL Voltage | 208
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP
Voltage (rated) | 208 |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V1-1 | LOBBY | A2 | 9X9 | 200 |  |  | 0
V1-2 | LOBBY | A2 | 9X9 | 200 |  |  | 0
V1-3 | 1g67 | B2 | 9X9 | 115 |  |  | 0
V1-4 | S3 | D1 | 12X6 | 85 |  |  | 0
|  |  |  | 600 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-C02
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-C02 |  | Area: CASINO FLR 2 ELEV LOBBY
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual
Model Num | FXSQ18TBVJU |  |  |  | SA CFM | 600
Serial Num |  |  |  |  | Fan RPM
[5 empty] | OA CFM | 90
[5 empty] | RA CFM | 510
Motor Data |  |  |  |  | RL Voltage | 208
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP
Voltage (rated) | 208 |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V2-1 | LOBBY | A2 | 9X9 | 185 |  |  | 0
V2-2 | LOBBY | A2 | 9X9 | 185 |  |  | 0
V2-3 | LOBBY | B2 | 9X9 | 145 |  |  | 0
V2-4 | STAIRS | D1 | 12X6 | 85 |  |  | 0
|  |  |  | 600 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-C03
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-C03 |  | Area: CASINO FLR G3 ELEV LOBBY
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual
Model Num | FXSQ18TBVJU |  |  |  | SA CFM | 600
Serial Num |  |  |  |  | Fan RPM
[5 empty] | OA CFM | 90
[5 empty] | RA CFM | 510
Motor Data |  |  |  |  | RL Voltage | 208
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP
Voltage (rated) | 208 |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V3-1 | LOBBY | A2 | 9X9 | 200 |  |  | 0
V3-2 | LOBBY | A2 | 9X9 | 200 |  |  | 0
V3-3 | LOBBY | B2 | 9X9 | 200 |  |  | 0
|  |  |  | 600 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-C04
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-C04 |  | Area: CASINO FLR G4 ELEV LOBBY
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual
Model Num | FXSQ18TBVJU |  |  |  | SA CFM | 600
Serial Num |  |  |  |  | Fan RPM
[5 empty] | OA CFM | 90
[5 empty] | RA CFM | 510
Motor Data |  |  |  |  | RL Voltage | 208
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP
Voltage (rated) | 208 |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V4-1 | LOBBY | A2 | 9X9 | 200 |  |  | 0
V4-2 | LOBBY | A2 | 9X9 | 200 |  |  | 0
V4-3 | LOBBY | B2 | 9X9 | 200 |  |  | 0
|  |  |  | 600 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## VRF-C05
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: VRF-C05 |  | Area: CASINO FLR G5 ELEV LOBBY
Unit Data |  |  |  |  | Test Data
MFG | DAIKIN |  |  |  |  | Design | Actual
Model Num | FXSQ18TBVJU |  |  |  | SA CFM | 600
Serial Num |  |  |  |  | Fan RPM
[5 empty] | OA CFM | 90
[5 empty] | RA CFM | 510
Motor Data |  |  |  |  | RL Voltage | 208
Motor MFG |  |  |  |  | RL Amperage
Horsepower |  |  |  |  | Suction ESP
Motor Rpm |  |  |  |  | Discharge ESP
Phase | 1 |  |  |  | Total ESP
Voltage (rated) | 208 |  |  |  | Brake HP
Amperage (rated)
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
V5-1 | LOBBY | A2 | 9X9 | 200 |  |  | 0
V5-2 | LOBBY | A2 | 9X9 | 200 |  |  | 0
V5-3 | LOBBY | B2 | 9X9 | 200 |  |  | 0
|  |  |  | 600 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## SF-C01
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: SF-C01 |  | Area: CASINO ENTRY VEST
Unit Data |  |  |  | Test Data
MFG | GREENHECK |  |  |  | Design | Actual
Model Num | SQ-100-VG |  |  | CFM | 750
Serial Num |  |  |  | SF RPM | 1316
Type | INLINE |  |  | RL Voltage | 115
Configuration |  |  |  | RL Amperage | 2.85
No. Filters / Size |  |  |  | Suction ESP
No. Filters / Size |  |  |  | Discharge ESP
|  |  |  | Total ESP | 0.5
|  |  |  | Brake Horse Power | 0.11
Motor Data
Motor MFG
Frame
Horsepower | 0.25
Motor Rpm | 1725
Phase | 1
Voltage (rated) | 115
Amperage (rated) | 2.85
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
S1-1 | 1h03 | E3 | 10 | 250 |  |  | 0
S1-2 | 1h03 | E3 | 10 | 250 |  |  | 0
S1-3 | 1h03 | E3 | 10 | 250 |  |  | 0
|  |  |  | 750 |  | 0 | 0

## SF-C02
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: SF-C02 |  | Area: 1g66 - ELECTRIC
Unit Data |  |  | Test Data
MFG | GREENHECK |  |  | Design | Actual
Model Num | SQ-80 |  | CFM | 200
Serial Num |  |  | SF RPM | 1283
Type | INLINE |  | RL Voltage | 115
Configuration |  |  | RL Amperage | 0.8
No. Filters / Size |  |  | Suction ESP
No. Filters / Size |  |  | Discharge ESP
|  |  | Total ESP | 0.3
|  |  | Brake Horse Power | 0.8
Motor Data
Motor MFG
Frame
Horsepower | 0.05
Motor Rpm | 1300
Phase | 1
Voltage (rated) | 115
Amperage (rated) | 0.8
Service Factor

## EF-C01
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-C01 |  |  | Area: CASINO RESTROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | CUE-160-B |  |  | CFM | 2310
Serial Num |  |  |  |  | Fan RPM | 1096
Type |  | CRE UPBLAST |  |  | RL Voltage | 115
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.7
Frame
Horsepower |  | 0.75
Motor Rpm |  | 1140
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 13.8
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E1-1 | 1g07 | J1 | 6X6 | 75 |  |  | 0
E1-2 | 1g07 | H1 | 8 | 150 |  |  | 0
E1-3 | 1g07 | H1 | 8 | 150 |  |  | 0
E1-4 | 1g07 | H1 | 8 | 150 |  |  | 0
E1-5 | 1g07 | H1 | 8 | 150 |  |  | 0
E1-6 | 1g07 | H1 | 8 | 150 |  |  | 0
E1-7 | 1g07 | H1 | 8 | 150 |  |  | 0
E1-8 | 1g09 | J1 | 6X6 | 75 |  |  | 0
E1-9 | 1g09 | H1 | 8 | 150 |  |  | 0
E1-10 | 1g09 | H1 | 8 | 150 |  |  | 0
E1-11 | 1g09 | H1 | 8 | 150 |  |  | 0
E1-12 | 1g09 | H1 | 8 | 150 |  |  | 0
E1-13 | 1g09 | H1 | 8 | 150 |  |  | 0
E1-14 | 1g09 | H1 | 8 | 150 |  |  | 0
E1-15 | 1g05 | G7 | 6X6 | 160 |  |  | 0
E1-16 | 1g03 | J1 | 6X6 | 50 |  |  | 0
E1-17 | 1g01A | G7 | 6X6 | 150 |  |  | 0
|  |  |  | 2310 |  | 0 | 0
-

## EF-C02
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-C02 |  |  | Area: CASINO BOH FLR 1 RESTROOMS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-100-A-3-1-19-X |  |  | CFM | 1030
Serial Num |  | 22891024 |  |  | Fan RPM | 1513
Type |  | CRE DNBLAST |  |  | RL Voltage | 115
[5 empty] | RL Amperage | 7.2
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  | MARATHON |  |  | Total ESP | 0.5
Frame |  | 56
Horsepower |  | 0.33
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 3.5
Service Factor |  | 1
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E2-1 | 1g30A | G5 | 12X12 | 480 |  |  | 0
E2-2 | 1g30B | J1 | 6X6 | 70 |  |  | 0
E2-3 | 1g31 | G5 | 12X12 | 480 |  |  | 0
|  |  |  | 1030 |  | 0 | 0
-

## EF-C03
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-C03 |  |  | Area: CASINO BOH FLR 2 RESTROOMS |  |  |  |  | NEED SUBMITTAL
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-100-A-3-1-19-X |  |  | CFM | 1175
Serial Num |  | 22891014 |  |  | Fan RPM | 1652
Type |  | CRE DNBLAST |  |  | RL Voltage | 115
[5 empty] | RL Amperage | 7.2
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  | MARATHON |  |  | Total ESP | 0.5
Frame |  | 56
Horsepower |  | 0.33
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 3.5
Service Factor |  | 1
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E3-1 | 2g22 | G5 | 12X12 | 450 |  |  | 0
E3-2 | 2g24 | J1 | 6X6 | 70 |  |  | 0
E3-3 | 2g32 | G7 | 6X6 | 40 |  |  | 0
E3-4 | 2g29 | G7 | 6X6 | 40 |  |  | 0
E3-5 | 2g30 |  |  | 125 |  |  | 0
E3-6 | 2g22 | G5 | 12X12 | 450 |  |  | 0
|  |  |  | 1175 |  | 0 | 0
-

## EF-C04
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-C04 |  |  | Area: DESTRUCTION (AREA D)
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-095-G |  |  | CFM | 425
Serial Num |  |  |  |  | Fan RPM | 1156
Type |  | CRE DNBLAST |  |  | RL Voltage | 115
[5 empty] | RL Amperage | 2
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.3
Frame
Horsepower |  | 0.09
Motor Rpm |  | 1300
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 2
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E4-1 | 1d70A | G5 | 12X12 | 425 |  |  | 0
|  |  |  | 425 |  | 0 | 0
-

## EF-C05
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-C05 |  | Area: GAMING EXPANSION (1h01)
Unit Data |  |  | Drive Data
MFG | GREENHECK |  | Motor Sheave Size | BP40
Model Num | GB-330-10-VG-1-46-X |  | Motor Bore Size | 0.875"
Serial Num | 22900456 |  | Fan Sheave Size | AK15-4
Type | CRE DNBLAST |  | Fan Bore Size | 1.25"
|  |  | Belt CL Distance | 11"
Motor Data |  |  | No of Belts | 1
Motor MFG | BALDOR RELIANCE |  | Belt Size | A52
Frame | 143T
Horsepower | 1 |  | Test Data
Motor Rpm | 1800 |  |  | Design | Actual
Phase | 3 |  | CFM | 6650
Voltage (rated) | 230 |  | Fan RPM | 358
Amperage (rated) | 2.4 |  | RL Voltage | 208
Service Factor | 1 |  | RL Amperage | 4.6
Suction ESP
|  |  | Total ESP | 0.3
|  |  | Brake Horse Power | 0.75
-

## EF-C06
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-C06 |  | Area: GAMING EXPANSION (1h01)
Unit Data |  |  | Drive Data
MFG | GREENHECK |  | Motor Sheave Size | BP40
Model Num | GB-330-10-VG-1-46-X |  | Motor Bore Size | 0.875"
Serial Num | 22900455 |  | Fan Sheave Size | AK15-4
Type | CRE DNBLAST |  | Fan Bore Size | 1.25"
|  |  | Belt CL Distance | 11"
Motor Data |  |  | No of Belts | 1
Motor MFG | BALDOR RELIANCE |  | Belt Size | A52
Frame | 143T
Horsepower | 1 |  | Test Data
Motor Rpm | 1800 |  |  | Design | Actual
Phase | 3 |  | CFM | 6650
Voltage (rated) | 230 |  | Fan RPM | 358
Amperage (rated) | 2.4 |  | RL Voltage | 208
Service Factor | 1 |  | RL Amperage | 4.6
Suction ESP
|  |  | Total ESP | 0.3
|  |  | Brake Horse Power | 0.75
-

## EF-C07
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-C07 |  | Area: GAMING EXPANSION (1h01)
Unit Data |  |  | Drive Data
MFG | GREENHECK |  | Motor Sheave Size | BP40
Model Num | GB-330-10-VG-1-46-X |  | Motor Bore Size | 0.875"
Serial Num | 22900457 |  | Fan Sheave Size | AK15-4
Type | CRE DNBLAST |  | Fan Bore Size | 1.25"
|  |  | Belt CL Distance | 11"
Motor Data |  |  | No of Belts | 1
Motor MFG | BALDOR RELIANCE |  | Belt Size | A52
Frame | 143T
Horsepower | 1 |  | Test Data
Motor Rpm | 1800 |  |  | Design | Actual
Phase | 3 |  | CFM | 6650
Voltage (rated) | 230 |  | Fan RPM | 358
Amperage (rated) | 2.4 |  | RL Voltage | 208
Service Factor | 1 |  | RL Amperage | 4.6
Suction ESP
|  |  | Total ESP | 0.3
|  |  | Brake Horse Power | 0.75
-

## EF-C08
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: EF-C08 |  | Area: GAMING EXPANSION (1h01)
Unit Data |  |  | Drive Data
MFG | GREENHECK |  | Motor Sheave Size | BP40
Model Num | GB-330-10-VG-1-46-X |  | Motor Bore Size | 0.875"
Serial Num | 22900454 |  | Fan Sheave Size | AK15-4
Type | CRE DNBLAST |  | Fan Bore Size | 1.25"
|  |  | Belt CL Distance | 11"
Motor Data |  |  | No of Belts | 1
Motor MFG | BALDOR RELIANCE |  | Belt Size | A52
Frame | 143T
Horsepower | 1 |  | Test Data
Motor Rpm | 1800 |  |  | Design | Actual
Phase | 3 |  | CFM | 6650
Voltage (rated) | 230 |  | Fan RPM | 358
Amperage (rated) | 2.4 |  | RL Voltage | 208
Service Factor | 1 |  | RL Amperage | 4.6
Suction ESP
|  |  | Total ESP | 0.3
|  |  | Brake Horse Power | 0.75
-

## SGRD
National TAB
Project: Harrah's River Valley Casino & Hotel
Address: 777 Casino Parkway Murphy, NC 28906
Asset: SUPPLY, EXHAUST, or RETURN
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!