## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8125 | 8122 | 6375 | 6320 | 1750 | 1802 | 21.54% | 22.19%
AC-2 | DRIVE THRU | 4375 | 4541 | 3300 | 3429 | 1075 | 1112 | 24.57% | 24.49%
AC-3 | DINING/RR | 5250 | 5195 | 3975 | 3884 | 1275 | 1311 | 24.29% | 25.24%
AC-4 | BOH | 1750 | 1724 | 1325 | 1294 | 425 | 430 | 24.29% | 24.94%
AC-5 | PLAY AREA |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
AC-6 | BOH |  |  | 0
EF-1 | HD 1 | [10 empty] | 1913 | 1969
EF-2 | HD 2 & 3 | [10 empty] | 1402 | 1369
EF-3 | RESTROOMS | [12 empty] | 300 | 283
EF4 | RESTROOMS | [12 empty] | 75 | 82
EF 5 | HD L1
TOTALS |  | 19500 | 19582 | 14975 | 14927 | 4525 | 4655 |  |  | 0 | 0 | 3315 | 3338 | 375 | 365
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4525 | 4655 |  | FRONT |  | 0.0098 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3690 | 3703 |  | SIDE |  | 0.0065 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 835 | 952 |  | REAR |  | 0.0057 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0073333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390