## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3000 | 2972 | 2700 | 2643 | 300 | 329 | 10% | 11.07%
RTU-2 | DINING | 5000 | 4914 | 4300 | 4196 | 700 | 718 | 14% | 14.61%
MUA-1 | HOOD 1 | [8 empty] | 1854 | 1774
KEF-1 | HOOD 1 | [10 empty] | 2317 | 2229
EF-1 | RESTROOMS | [12 empty] | 120 | 112
EF-2 | RESTROOMS | [12 empty] | 120 | 117
TOTALS |  | 8000 | 7886 | 7000 | 6839 | 1000 | 1047 |  |  | 1854 | 1774 | 2317 | 2229 | 240 | 229
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2854 | 2821 |  | FRONT |  | 0.0082 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2557 | 2458 |  | SIDE |  | 0.0052 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 297 | 363 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0067 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0