## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
DOAS-1 | KITCHEN | 3250 | 3363 | 0 | 0 | 3250 | 3363 | 100% | 100%
RTU-1 | BAR/DINGING | 4000 | 4175 | 3125 | 3304 | 875 | 871 | 21.88% | 20.86%
RTU-2 | DINING | 4000 | 4218 | 3125 | 3333 | 875 | 885 | 21.88% | 20.98%
EF-1 | HD-1 | [10 empty] | 1800 | 1847
EF-2 | HD-2 | [10 empty] | 2025 | 2034
EF-3 | HD-3 | [10 empty] | 525 | 523
EF-4 | RESTROOMS | [12 empty] | 300 | 310
TOTALS |  | 11250 | 11756 | 6250 | 6637 | 5000 | 5119 |  |  | 0 | 0 | 4350 | 4404 | 300 | 310
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 5000 | 5119 |  | FRONT |  | 0.008 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 4650 | 4714 |  | SIDE |  | 0.01 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 350 | 405 |  | REAR |  | 0.008 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0086667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0