## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
WSHP-1 | KITCHEN | 4000 | 2641 | 4000 | 2641 |  |  | 0% | 0%
WSHP-2 | KITCHEN | 4000 | 2017 | 4000 | 2017 |  |  | 0% | 0%
WSHP-3 | DINING | 4000 | 2711 | 4000 | 2711 |  |  | 0% | 0%
WSHP-4 | DINING | 4000 | 2639 | 4000 | 2639 |  |  | 0% | 0%
MUA-1 | KITCHEN HD | [8 empty] | 4313 | 3270
PCU-1 | KITCHEN HD 2&3 | [10 empty] | 3013 | 2418
EF-1 | KITCHEN HD 1 | [10 empty] | 1300 | 1139
EF-2 | RESTROOM | [12 empty] | 215 | 211
EF-3 | RESTROOM | [12 empty] | 215 | 209
TOTALS |  | 16000 | 10008 | 16000 | 10008 | 0 | 0 |  |  | 4313 | 3270 | 4313 | 3557 | 430 | 420
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4313 | 3270 |  | FRONT | [10 empty] | #DIV/0! | #DIV/0! | TRUE
TOTAL EXHAUST |  | 4743 | 3977 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | -430 | -707 |  | REAR | [10 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0