## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8125 | 8094 | 6375 | 6472 | 1750 | 1622 | 21.54% | 20.04%
AC-2 | DRIVE THRU | 4375 | 4599 | 3300 | 3525 | 1075 | 1074 | 24.57% | 23.35%
AC-3 | DINNING/ RR | 5250 | 5453 | 3975 | 4255 | 1275 | 1198 | 24.29% | 21.97%
AC-4 | BOH | 1750 | 1805 | 1325 | 1371 | 425 | 434 | 24.29% | 24.04%
AC-5 | PLAY AREA |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
AC-6 | BOH |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
EF-1 | HD 1 | [10 empty] | 1913 | 0
EF-2 | HD 2 & 3 | [10 empty] | 1402 | 1373
EF-3 | RESTROOMS | [12 empty] | 300 | 301
EF4 | RESTROOMS | [12 empty] | 75 | 69
TOTALS |  | 19500 | 19951 | 14975 | 15623 | 4525 | 4328 |  |  | 0 | 0 | 3315 | 1373 | 300 | 301
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4525 | 4328 |  | FRONT |  | 0.024 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3615 | 1674 |  | SIDE |  | 0.059 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 910 | 2654 |  | REAR |  | 0.06 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.047667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390