## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 9288 | 7500 | 7431 | 2000 | 1857 | 21.05% | 19.99%
AC-2 | DINING A, RR | 2500 | 2615 | 1975 | 2125 | 525 | 490 | 21% | 18.74%
AC-3 | DINING B | 4000 | 3615 | 3000 | 2647 | 1000 | 968 | 25% | 26.78%
AC-4 | DINING B | 2765 | 2710 | 2165 | 2164 | 600 | 546 | 21.7% | 20.15%
AC-5 | PLAY AREA | 1800 | 1651 | 1500 | 1329 | 300 | 322 | 16.67% | 19.5%
AC-6 | BOH | 1200 | 1188 | 1080 | 1052 | 120 | 136 | 10% | 11.45%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1813
EF-2 | HOOD 2 | [10 empty] | 701 | 702
EF-3 | RESTROOMS | [12 empty] | 500 | 0
EF-4 | HOOD 3 | [10 empty] | 701 | 708
TOTALS |  | 21765 | 21067 | 17220 | 16748 | 4545 | 4319 |  |  | 0 | 0 | 3314 | 3223 | 500 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4545 | 4319 |  | FRONT |  | 0.016 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3814 | 3223 |  | SIDE |  | 0.021 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 731 | 1096 |  | REAR |  | 0.017 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.018 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390