## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | SALES | 14000 | 14063 | 9000 | 11979 | 5000 | 2084 | 35.71% | 14.82%
RTU-2 | BRK ROOM | 800 | 724 | 600 | 620 | 200 | 104 | 25% | 14.36%
RTU-3 | BAKERY | 4000 | 3641 | 3000 | 3263 | 1000 | 378 | 25% | 10.38%
RTU-4 | DELI | 3000 | 3219 | 2250 | 2935 | 750 | 284 | 25% | 8.823%
RTU-5 | PHARM. | 800 | 738 | 600 | 637 | 200 | 101 | 25% | 13.69%
RTU-6 | SALES | 8000 | 8700 | 6000 | 8700 | 2000 | 0 | 25% | 0%
RTU-7 | SALES | 8000 | 8000 | 6000 | 7104 | 2000 | 896 | 25% | 11.2%
RTU-8 | LIQ. DEPT | 3000 | 3523 | 2250 | 3113 | 750 | 410 | 25% | 11.64%
RTU-9 | OLO | 800 | 538 | 600 | 448 | 200 | 90 | 25% | 16.73%
RTU-10 | ENTRY VEST. | 1600 | 1568 | 1200 | 1396 | 400 | 172 | 25% | 10.97%
RTU-11 | PRODUCE | 6000 | 6600 | 4500 | 5913 | 1500 | 687 | 25% | 10.41%
MUA-1 | HOOD | [8 empty] | 2300 | 1186
EF-1 | KH-1 | [10 empty] | 2829 | 2632
EF-2 | KH-2 | [10 empty] | 1923 | 0
EF-3 | KH-3 | [10 empty] | 967 | 1526
EF-4 | KH-4 | [10 empty] | 810 | 0
EF-5 | KH-5 | [10 empty] | 750 | 854
EF-8 | TOILET EXH. | [12 empty] | 675 | 0
EF-10 | UNI. TOILET. | [12 empty] | 75 | 0
TOTALS |  | 50000 | 51314 | 36000 | 46108 | 14000 | 5206 |  |  | 2300 | 1186 | 7279 | 5012 | 750 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 16300 | 6392 |  | FRONT |  | 0.012 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 8029 | 5012 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 8271 | 1380 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.012 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
[1] Building Pressure Measured at OLO door in main vestibule. [2] RTU-8 economizer not functional-unable to set [3] EF-2 / EF-4 not used, hoods have no cooking equipment installed. [3] Restroom Exhaust not functional.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0