## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AHU1-1 | BOH | 1050 | 1109 | 939 | 992 | 111 | 117 | 10.57% | 10.55%
AHU1-2 | BOH | 1050 | 1094 | 939 | 975 | 111 | 119 | 10.57% | 10.88%
AHU2-1 | KITCHEN | 1500 | 1643 | 0 | 1464 | 168 | 179 | 11.2% | 10.89%
AHU3-1 | DINING | 1200 | 1265 | 0 | 972 | 303 | 293 | 25.25% | 23.16%
AHU3-2 | DINING | 1200 | 1280 | 0 | 992 | 303 | 288 | 25.25% | 22.5%
AHU3-3 | DINING | 1200 | 1201 | 0 | 891 | 303 | 310 | 25.25% | 25.81%
IU1-1 | BOH | 300 | 0 | 0 | 0 | 0 | 0 | 0% | #DIV/0!
IU1-2 | BOH | 300 | 0 | 0 | 0 | 0 | 0 | 0% | #DIV/0!
IU2-1 | BOH | 400 | 0 | 0 | 0 | 0 | 0 | 0% | #DIV/0!
IU3-1 | BOH | 500 | 0 | 0 | 0 | 0 | 0 | 0% | #DIV/0!
IU3-2 | BOH | 500 | 0 | 0 | 0 | 0 | 0 | 0% | #DIV/0!
MUA-1 | KITCHEN HOOD | [8 empty] | 2250 | 2308
EF-1 | KITCHEN HOOD | [10 empty] | 3200 | 3233
EF-2 | RESTROOM | [12 empty] | 250 | 256
TOTALS |  | 9200 | 7592 | 1878 | 6286 | 1299 | 1306 |  |  | 2250 | 2308 | 3200 | 3233 | 250 | 256
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3549 | 3614 |  | FRONT |  | 0.0033 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3450 | 3489 |  | SIDE |  | 0.0009 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 99 | 125 |  | REAR |  | 0.0004 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0015333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 177X12 |  | 2250 |  | 3200 |  | -950