## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3900 | 3864 | 2300 | 2252 | 1600 | 1612 | 41.03% | 41.72%
RTU-2 | KITCHEN | 2600 | 2636 | 1900 | 1925 | 700 | 711 | 26.92% | 26.97%
RTU-3 | KITCHEN | 2600 | 2641 | 1900 | 1938 | 700 | 703 | 26.92% | 26.62%
FCU-1 | MANAGERS OFFICE |  |  |  |  | 40 | 41
KEF-1 | GRILL HD | [10 empty] | 860 | 850
KEF-2 | FRY HD | [10 empty] | 1200 | 1237
EF-3 | RESTROOMS | [12 empty] | 450 | 456
TOTALS |  | 9100 | 9141 | 6100 | 6115 | 3040 | 3067 |  |  | 0 | 0 | 2060 | 2087 | 450 | 456
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3040 | 3067 |  | FRONT |  | 0.0048 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2510 | 2543 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 530 | 524 |  | REAR |  | 0.0021 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00345 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 1440 | 1455
TOTAL KITCHEN EXHAUST |  | 2060 | 2087
NET AIRFLOW |  | -620 | -632
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0