## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3200 | 3190 | 1350 | 1332 | 1850 | 1858 | 57.81% | 58.24%
RTU-2 | KITCHEN SOUTH | 3200 | 3197 | 0 | 0 | 3200 | 3197 | 100% | 100%
RTU-3 | KITCHEN NORTH | 2800 | 2897 | 1475 | 1558 | 1325 | 1339 | 47.32% | 46.22%
EF-1 | HD1 & HD2 | [10 empty] | 4025 | 3916
EF-2 | HD3 | [10 empty] | 2025 | 2020
EF-3 | CO2 | [12 empty] | 200 | 189
EF-4 | RESTROOMS | [12 empty] | 150 | 147
TOTALS |  | 9200 | 9284 | 2825 | 2890 | 6375 | 6394 |  |  | 0 | 0 | 6050 | 5936 | 350 | 336
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | TRUE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 6375 | 6394 |  | FRONT |  | 0.004 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 6400 | 6272 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -25 | 122 |  | REAR |  | 0.004 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.004 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0